## Notes
Notes:
1 | The password to these spreadsheets is, "password".
2 | The bright yellow cells are not protected.
3 | These spreadsheets were built for my use. They might not match your uses.
4 | Sometimes a calculation is just a calculation.
5 | There are a lot of rules related to doing electrical work. Learn them and use them before using these spreadsheets.
6 | You are responsible for your own work.
7 | Double check my calculations. I'm not perfect.
8 | Updates are occasionally available at this website: |  | http://www.risingedgeservices.com/index.html
9 | Yellow tabs = | Good Stuff
10 | Orange tabs = | So, So
11 | Purple tabs = | Older Sheets or Less Interesting Stuff
12 | I would love to hear your constructive criticism of my work. I'd want to correct any errors or omissions in these spreadsheets.
13 | You are free to use and modify my spreadsheets. Nothing here is that original.
14 | If you have any comments, please contact me at risingedgeservices@gmail.com
Spreadsheet by:
Lorn MacIlravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## Ref.
AWG | Cmils |  | MOTOR SPEED |  |  | STANDARD OC |  | GROUNDING
18 | 1620 |  | BASE HZ | 60 |  | 1 | 175 | OC Device | CU | AL
16 | 2580 |  | POLES | RPM |  | 3 | 200 | 15 | 14 | 12
14 | 4110 |  | 2 | 3600 |  | 6 | 225 | 20 | 12 | 10
12 | 6530 |  | 4 | 1800 |  | 10 | 250 | 30 | 10 | 8
10 | 10380 |  | 6 | 1200 |  | 15 | 300 | 40 | 10 | 8
8 | 16510 |  | 8 | 900 |  | 20 | 350 | 60 | 10 | 8
6 | 26240 |  | 10 | 720 |  | 25 | 400 | 100 | 8 | 6
4 | 41740 |  | 12 | 600 |  | 30 | 450 | 200 | 6 | 4
3 | 52620 |  | 14 | 514.2857 |  | 35 | 500 | 300 | 4 | 2
2 | 66360 |  | 16 | 450 |  | 40 | 600 | 400 | 3 | 1
1 | 83690 |  |  |  |  | 45 | 700 | 500 | 2 | 1/O
1/O | 105600 |  |  |  |  | 50 | 800 | 600 | 1 | 2/O
2/O | 133100 |  | # WIRES | % |  | 60 | 1000 | 800 | 1/O | 3/O
3/O | 167800 |  | 4-6 | 80 |  | 70 | 1200 | 1000 | 2/O | 4/O
4/O | 211600 |  | 7-9 | 70 |  | 80 | 1600 | 1200 | 3/O | 250
250 | 250000 |  | 10-20 | 50 |  | 90 | 2000 | 1600 | 4/O | 350
|  |  | 21-30 | 45 |  | 100 | 2500 | 2000 | 250 | 400
|  |  | 31-40 | 40 |  | 110 | 3000 | 2500 | 350 | 600
|  |  | 41 + | 35 |  | 125 | 4000 | 3000 | 400 | 600
[6 empty] | 150 | 5000
From Table 310.15 (B)(16) | [8 empty] | AWG | Cmils
| CU |  |  | AL |  |  |  |  | 18 AWG | 1620
AWG | 60C | 75C | 90C | 60C | 75C | 90C | AWG |  | 16 AWG | 2580
14 | 15 | 20 | 25 | -- | -- | -- | 14 |  | 14 AWG | 4110
12 | 20 | 25 | 30 | 15 | 20 | 25 | 12 |  | 12 AWG | 6530
10 | 30 | 35 | 40 | 25 | 30 | 35 | 10 |  | 10 AWG | 10380
8 | 40 | 50 | 55 | 35 | 40 | 45 | 8 |  | 8 AWG | 16510
6 | 55 | 65 | 75 | 40 | 50 | 55 | 6 |  | 6 AWG | 26240
4 | 70 | 85 | 95 | 55 | 65 | 75 | 4 |  | 4 AWG | 41740
3 | 85 | 100 | 115 | 65 | 75 | 85 | 3 |  | 3 AWG | 52620
2 | 95 | 115 | 130 | 75 | 90 | 100 | 2 |  | 2 AWG | 66360
1 | 110 | 130 | 145 | 85 | 100 | 115 | 1 |  | 1 AWG | 83690
1/O | 125 | 150 | 170 | 100 | 120 | 135 | 1/O |  | 1/O AWG | 105600
2/O | 145 | 175 | 195 | 115 | 135 | 150 | 2/O |  | 2/O AWG | 133100
3/O | 165 | 200 | 225 | 130 | 155 | 175 | 3/O |  | 3/O AWG | 167800
4/O | 195 | 230 | 260 | 150 | 180 | 205 | 4/O |  | 4/O AWG | 211600
250 | 215 | 255 | 290 | 170 | 205 | 230 | 250 |  | 250 KCIML | 250000
300 | 240 | 285 | 320 | 195 | 230 | 260 | 300 |  | 300 KCIML | 300000
350 | 260 | 310 | 350 | 210 | 250 | 280 | 350 |  | 350 KCIML | 350000
400 | 280 | 335 | 380 | 225 | 270 | 305 | 400 |  | 400 KCIML | 400000
500 | 320 | 380 | 430 | 260 | 310 | 350 | 500 |  | 500 KCIML | 500000
600 | 350 | 420 | 475 | 285 | 340 | 385 | 600 |  | 600 KCIML | 600000
700 | 385 | 460 | 520 | 315 | 375 | 425 | 700 |  | 700 KCIML | 700000
750 | 400 | 475 | 535 | 320 | 385 | 435 | 750 |  | 750 KCIML | 750000
800 | 410 | 490 | 555 | 330 | 395 | 445 | 800 |  | 800 KCIML | 800000
900 | 435 | 520 | 585 | 355 | 425 | 480 | 900 |  | 900 KCIML | 900000
1000 | 455 | 545 | 615 | 375 | 445 | 500 | 1000 |  | 1000 KCIML | 1000000
1250 | 495 | 590 | 665 | 405 | 485 | 545 | 1250 |  | 1250 KCIML | 1250000
1500 | 525 | 625 | 705 | 435 | 520 | 585 | 1500 |  | 1500 KCIML | 1500000
1750 | 545 | 650 | 735 | 455 | 545 | 615 | 1750 |  | 1750 KCIML | 1750000
2000 | 555 | 665 | 750 | 470 | 560 | 630 | 2000 |  | 2000 KCIML | 2000000
Source: NEC 2014

## Fuses and OL
Overload Calculation |  |  |  | 2016-11-02
NP AMPS | 150
OL 140% | 210 | 140% NPA | STANDARD OC
OL 130% | 195 | 130% NPA | 1 | 175
SF 1.15 & 40°C | 187.5 | 125% NPA | 3 | 200
All other motors | 172.5 | 115% NPA | 6 | 225
UC 90% | 135 | 90% NPA | 10 | 250
UC 85% | 127.5 | 85% NPA | 15 | 300
|  |  | 20 | 350
Fuse and Breaker Selection |  |  | 25 | 400
NEC AMPS | 135 |  | 30 | 450
Min. Feeder Amps | 168.75 | 125% | 35 | 500
|  |  | 40 | 600
AC 3Ø |  |  | 45 | 700
Non-time delay | 405 | 300% | 50 | 800
Dual Element | 236.25 | 175% | 60 | 1000
Instant Trip CB | 1080 | 800% | 70 | 1200
IT Breaker | 337.5 | 250% | 80 | 1600
|  |  | 90 | 2000
Design E |  |  | 100 | 2500
Non-time delay | 405 | 300% | 110 | 3000
Dual Element | 236.25 | 175% | 125 | 4000
Instant Trip CB | 1485 | 1100% | 150 | 5000
IT Breaker | 337.5 | 250%
Notes:
AC 1Ø |  |  | Write your notes here.
Non-time delay | 405 | 300%
Dual Element | 236.25 | 175%
Instant Trip CB | 1080 | 800%
IT Breaker | 337.5 | 250%
Synchronous
Non-time delay | 405 | 300%
Dual Element | 236.25 | 175%
Instant Trip CB | 1080 | 800%
IT Breaker | 337.5 | 250%
Wound Rotor
Non-time delay | 202.5 | 150%
Dual Element | 150 | 150%
Instant Trip CB | 1080 | 800%
IT Breaker | 202.5 | 150%
Direct Current |  |  | Spreadsheet by:
Non-time delay | 202.5 | 150% | Lorn Macilravie, Master Electrician
Dual Element | 202.5 | 150% | risingedgeservices@gmail.com
Instant Trip CB | 337.5 | 250% | Mobile: 307-696-7926
IT Breaker | 202.5 | 150% | The YELLOW cells are not protected.

## Max Amps
MAX AMPS TO KEEP VOLTAGE DROP UNDER A DEFINED % VOLTAGE DROP | [14 empty] | 2016-10-28
Phase | 1.732 | Use 1.732 or 2
Volts | 480 | Use the actual voltage at the power drop
%VD | 5% | %VD | [5 empty] | 24 | Voltage Drop
Table 310.15(B)(16)
| Based on 75C CU |  | Copper Conductors
AWG | MAX AMPS | CMILS | 150 | 250 | 500 | 750 | 1000 | 1500 | 2000 | 2500 | 3000 | 3500 | 4000 | 4500 | 5000 | 5280 | FEET
14* | 20 | 4110 | 29.4323 | 17.6594 | 8.8297 | 5.8865 | 4.4148 | 2.9432 | 2.2074 | 1.7659 | 1.4716 | 1.2614 | 1.1037 | 0.98108 | 0.88297 | 0.83614
12* | 25 | 6530 | 46.7623 | 28.0574 | 14.0287 | 9.3525 | 7.0143 | 4.6762 | 3.5072 | 2.8057 | 2.3381 | 2.0041 | 1.7536 | 1.5587 | 1.4029 | 1.3285
10* | 35 | 10380 | 74.3327 | 44.5996 | 22.2998 | 14.8665 | 11.1499 | 7.4333 | 5.575 | 4.46 | 3.7166 | 3.1857 | 2.7875 | 2.4778 | 2.23 | 2.1117
8 | 50 | 16510 | 118.2305 | 70.9383 | 35.4691 | 23.6461 | 17.7346 | 11.823 | 8.8673 | 7.0938 | 5.9115 | 5.067 | 4.4336 | 3.941 | 3.5469 | 3.3588
6 | 35 | 26240 | 187.9084 | 112.745 | 56.3725 | 37.5817 | 28.1863 | 18.7908 | 14.0931 | 11.2745 | 9.3954 | 8.0532 | 7.0466 | 6.2636 | 5.6373 | 5.3383
4 | 85 | 41740 | 298.9061 | 179.3437 | 89.6718 | 59.7812 | 44.8359 | 29.8906 | 22.418 | 17.9344 | 14.9453 | 12.8103 | 11.209 | 9.9635 | 8.9672 | 8.4917
3 | 100 | 52620 | 376.8194 | 226.0916 | 113.0458 | 75.3639 | 56.5229 | 37.6819 | 28.2615 | 22.6092 | 18.841 | 16.1494 | 14.1307 | 12.5606 | 11.3046 | 10.7051
2 | 115 | 66360 | 475.2135 | 285.1281 | 142.564 | 95.0427 | 71.282 | 47.5213 | 35.641 | 28.5128 | 23.7607 | 20.3663 | 17.8205 | 15.8404 | 14.2564 | 13.5004
1 | 130 | 83690 | 599.3161 | 359.5897 | 179.7948 | 119.8632 | 89.8974 | 59.9316 | 44.9487 | 35.959 | 29.9658 | 25.685 | 22.4744 | 19.9772 | 17.9795 | 17.026
1/O | 150 | 105600 | 756.2168 | 453.7301 | 226.865 | 151.2434 | 113.4325 | 75.6217 | 56.7163 | 45.373 | 37.8108 | 32.4093 | 28.3581 | 25.2072 | 22.6865 | 21.4834
2/O | 175 | 133100 | 953.1482 | 571.8889 | 285.9445 | 190.6296 | 142.9722 | 95.3148 | 71.4861 | 57.1889 | 47.6574 | 40.8492 | 35.7431 | 31.7716 | 28.5944 | 27.0781
3/O | 200 | 167800 | 1201.6399 | 720.9839 | 360.492 | 240.328 | 180.246 | 120.164 | 90.123 | 72.0984 | 60.082 | 51.4989 | 45.0615 | 40.0547 | 36.0492 | 34.1375
4/O | 230 | 211600 | 1515.298 | 909.1788 | 454.5894 | 303.0596 | 227.2947 | 151.5298 | 113.6473 | 90.9179 | 75.7649 | 64.9413 | 56.8237 | 50.5099 | 45.4589 | 43.0482
250 | 255 | 250000 | 1790.2859 | 1074.1715 | 537.0858 | 358.0572 | 268.5429 | 179.0286 | 134.2714 | 107.4172 | 89.5143 | 76.7265 | 67.1357 | 59.6762 | 53.7086 | 50.8604
300 | 285 | 300000 | 2148.3431 | 1289.0059 | 644.5029 | 429.6686 | 322.2515 | 214.8343 | 161.1257 | 128.9006 | 107.4172 | 92.0718 | 80.5629 | 71.6114 | 64.4503 | 61.0325
350 | 310 | 350000 | 2506.4003 | 1503.8402 | 751.9201 | 501.2801 | 375.96 | 250.64 | 187.98 | 150.384 | 125.32 | 107.4172 | 93.99 | 83.5467 | 75.192 | 71.2046
400 | 335 | 400000 | 2864.4575 | 1718.6745 | 859.3372 | 572.8915 | 429.6686 | 286.4457 | 214.8343 | 171.8674 | 143.2229 | 122.7625 | 107.4172 | 95.4819 | 85.9337 | 81.3766
500 | 380 | 500000 | 3580.5718 | 2148.3431 | 1074.1715 | 716.1144 | 537.0858 | 358.0572 | 268.5429 | 214.8343 | 179.0286 | 153.4531 | 134.2714 | 119.3524 | 107.4172 | 101.7208
600 | 420 | 600000 | 4296.6862 | 2578.0117 | 1289.0059 | 859.3372 | 644.5029 | 429.6686 | 322.2515 | 257.8012 | 214.8343 | 184.1437 | 161.1257 | 143.2229 | 128.9006 | 122.0649
700 | 460 | 700000 | 5012.8005 | 3007.6803 | 1503.8402 | 1002.5601 | 751.9201 | 501.2801 | 375.96 | 300.768 | 250.64 | 214.8343 | 187.98 | 167.0934 | 150.384 | 142.4091
750 | 475 | 750000 | 5370.8577 | 3222.5146 | 1611.2573 | 1074.1715 | 805.6287 | 537.0858 | 402.8143 | 322.2515 | 268.5429 | 230.1796 | 201.4072 | 179.0286 | 161.1257 | 152.5812
| 60 | 500000 | 3580.5718 | 2148.3431 | 1074.1715 | 716.1144 | 537.0858 | 358.0572 | 268.5429 | 214.8343 | 179.0286 | 153.4531 | 134.2714 | 119.3524 | 107.4172 | 101.7208
Table 310.15(B)(16)
| Based on 75C AL |  | Aluminum Conductors
AWG | MAX AMPS | CMILS | 150 | 250 | 500 | 750 | 1000 | 1500 | 2000 | 2500 | 3000 | 3500 | 4000 | 4500 | 5000 | 5280 | FEET
12* | 20 | 6530 | 28.4544 | 17.0726 | 8.5363 | 5.6909 | 4.2682 | 2.8454 | 2.1341 | 1.7073 | 1.4227 | 1.2195 | 1.067 | 0.94848 | 0.85363 | 0.80836
10* | 30 | 10380 | 45.2307 | 27.1384 | 13.5692 | 9.0461 | 6.7846 | 4.5231 | 3.3923 | 2.7138 | 2.2615 | 1.9385 | 1.6962 | 1.5077 | 1.3569 | 1.285
8 | 40 | 16510 | 71.9421 | 43.1653 | 21.5826 | 14.3884 | 10.7913 | 7.1942 | 5.3957 | 4.3165 | 3.5971 | 3.0832 | 2.6978 | 2.3981 | 2.1583 | 2.0438
6 | 50 | 26240 | 114.3405 | 68.6043 | 34.3021 | 22.8681 | 17.1511 | 11.434 | 8.5755 | 6.8604 | 5.717 | 4.9003 | 4.2878 | 3.8113 | 3.4302 | 3.2483
4 | 65 | 41740 | 181.8816 | 109.1289 | 54.5645 | 36.3763 | 27.2822 | 18.1882 | 13.6411 | 10.9129 | 9.0941 | 7.7949 | 6.8206 | 6.0627 | 5.4564 | 5.1671
3 | 75 | 52620 | 229.291 | 137.5746 | 68.7873 | 45.8582 | 34.3937 | 22.9291 | 17.1968 | 13.7575 | 11.4646 | 9.8268 | 8.5984 | 7.643 | 6.8787 | 6.5139
2 | 90 | 66360 | 289.1629 | 173.4978 | 86.7489 | 57.8326 | 43.3744 | 28.9163 | 21.6872 | 17.3498 | 14.4581 | 12.3927 | 10.8436 | 9.6388 | 8.6749 | 8.2149
1 | 100 | 83690 | 364.6782 | 218.8069 | 109.4035 | 72.9356 | 54.7017 | 36.4678 | 27.3509 | 21.8807 | 18.2339 | 15.6291 | 13.6754 | 12.1559 | 10.9403 | 10.3602
1/O | 120 | 105600 | 460.1508 | 276.0905 | 138.0452 | 92.0302 | 69.0226 | 46.0151 | 34.5113 | 27.609 | 23.0075 | 19.7207 | 17.2557 | 15.3384 | 13.8045 | 13.0725
2/O | 135 | 133100 | 579.9817 | 347.989 | 173.9945 | 115.9963 | 86.9973 | 57.9982 | 43.4986 | 34.7989 | 28.9991 | 24.8564 | 21.7493 | 19.3327 | 17.3995 | 16.4768
3/O | 155 | 167800 | 731.1865 | 438.7119 | 219.356 | 146.2373 | 109.678 | 73.1187 | 54.839 | 43.8712 | 36.5593 | 31.3366 | 27.4195 | 24.3729 | 21.9356 | 20.7723
4/O | 180 | 211600 | 922.0445 | 553.2267 | 276.6134 | 184.4089 | 138.3067 | 92.2045 | 69.1533 | 55.3227 | 46.1022 | 39.5162 | 34.5767 | 30.7348 | 27.6613 | 26.1944
250 | 205 | 250000 | 1089.3721 | 653.6233 | 326.8116 | 217.8744 | 163.4058 | 108.9372 | 81.7029 | 65.3623 | 54.4686 | 46.6874 | 40.8515 | 36.3124 | 32.6812 | 30.9481
300 | 230 | 300000 | 1307.2465 | 784.3479 | 392.174 | 261.4493 | 196.087 | 130.7247 | 98.0435 | 78.4348 | 65.3623 | 56.0249 | 49.0217 | 43.5749 | 39.2174 | 37.1377
350 | 250 | 350000 | 1525.1209 | 915.0726 | 457.5363 | 305.0242 | 228.7681 | 152.5121 | 114.3841 | 91.5073 | 76.256 | 65.3623 | 57.192 | 50.8374 | 45.7536 | 43.3273
400 | 270 | 400000 | 1742.9953 | 1045.7972 | 522.8986 | 348.5991 | 261.4493 | 174.2995 | 130.7247 | 104.5797 | 87.1498 | 74.6998 | 65.3623 | 58.0998 | 52.2899 | 49.5169
500 | 310 | 500000 | 2178.7442 | 1307.2465 | 653.6233 | 435.7488 | 326.8116 | 217.8744 | 163.4058 | 130.7247 | 108.9372 | 93.3748 | 81.7029 | 72.6248 | 65.3623 | 61.8961
600 | 340 | 600000 | 2614.493 | 1568.6958 | 784.3479 | 522.8986 | 392.174 | 261.4493 | 196.087 | 156.8696 | 130.7247 | 112.0497 | 98.0435 | 87.1498 | 78.4348 | 74.2754
700 | 375 | 700000 | 3050.2418 | 1830.1451 | 915.0726 | 610.0484 | 457.5363 | 305.0242 | 228.7681 | 183.0145 | 152.5121 | 130.7247 | 114.3841 | 101.6747 | 91.5073 | 86.6546
750 | 385 | 750000 | 3268.1163 | 1960.8698 | 980.4349 | 653.6233 | 490.2174 | 326.8116 | 245.1087 | 196.087 | 163.4058 | 140.0621 | 122.5544 | 108.9372 | 98.0435 | 92.8442
| 60 | 500000 | 2178.7442 | 1307.2465 | 653.6233 | 435.7488 | 326.8116 | 217.8744 | 163.4058 | 130.7247 | 108.9372 | 93.3748 | 81.7029 | 72.6248 | 65.3623 | 61.8961
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.
1.732
2
21.2
12.9

## VD 2
Voltage Drop Calculator |  | 2016-11-02
470 | Volts |  | AWG | Cmils | 1/O AWG
60 | Amperes |  | 18 AWG | 1620
2500 | Distance (Feet) |  | 16 AWG | 2580
1/O AWG | Wire Size Drop Down |  | 14 AWG | 4110
105600 | CMILS |  | 12 AWG | 6530
|  |  | 10 AWG | 10380
6.753% | Percent Voltage Drop, CU, 3 Phase |  | 8 AWG | 16510
31.7369 | Volts Dropped, CU, 3 Phase |  | 6 AWG | 26240
438.2631 | Volts (Out) |  | 4 AWG | 41740
|  |  | 3 AWG | 52620
11.1% | Percent Voltage Drop, AL, 3 Phase |  | 2 AWG | 66360
52.1568 | Volts Dropped, AL, 3 Phase |  | 1 AWG | 83690
417.8432 | Volts (Out) |  | 1/O AWG | 105600
|  |  | 2/O AWG | 133100
7.797% | Percent Voltage Drop, CU, Single Phase |  | 3/O AWG | 167800
36.6477 | Volts Dropped, CU, Single Phase |  | 4/O AWG | 211600
433.3523 | Volts (Out) |  | 250 KCIML | 250000
|  |  | 300 KCIML | 300000
12.81% | Percent Voltage Drop, AL, Single Phase |  | 350 KCIML | 350000
60.2273 | Volts Dropped, AL, Single Phase |  | 400 KCIML | 400000
409.7727 | Volts (Out) |  | 500 KCIML | 500000
|  |  | 600 KCIML | 600000
K=12.9 for CU and K=21.2 for AL |  |  | 700 KCIML | 700000
1.73 X I X L X K / Cmils = VD 3 Phase |  |  | 750 KCIML | 750000
2 X I X L X K / Cmils = VD Single Phase |  |  | 800 KCIML | 800000
( VD / E ) x 100 = %VD |  |  | 900 KCIML | 900000
|  |  | 1000 KCIML | 1000000
Spreadsheet by: |  |  | 1250 KCIML | 1250000
Lorn Macilravie, Master Electrician |  |  | 1500 KCIML | 1500000
risingedgeservices@gmail.com |  |  | 1750 KCIML | 1750000
Mobile: 307-696-7926 |  |  | 2000 KCIML | 2000000
The YELLOW cells are not protected.

## HP KVA KW 2
COMMON ELECTRICAL FORMULAS |  |  |  | 2016-11-02 | A | 3.14 | 0.5
[5 empty] | B | 3.54 | 0.75
1 | 200 | HP (Horse Power) |  |  | C | 3.99 | 1
2 | 0.8 | PF (Power Factor) |  |  | D | 4.49 | 1.5
3 | 0.9 | EFF (Efficiency) |  |  | E | 4.99 | 2
4 | 3 | KW (Kilowatts) |  |  | F | 5.59 | 3
5 | 20 | KVA (Kilovolt Amps) |  |  | G | 6.29 | 5
6 | 480 | E (Volts) |  |  | H | 7.09 | 7.5
7 | 130 | I (Amps) |  |  | J | 7.99 | 10
8 | D | KVA/HP (Locked Rotor Code) = | 4.49 |  | K | 8.99 | 15
9 |  |  |  |  | L | 9.99 | 20
10 |  |  |  |  | M | 11.19 | 25
11 | 3 Phase |  | 3 Phase Calculation | 3 Phase Formula | N | 12.49 | 30
12 | Amps from HP | 249.2569 | 249.26 = (200 X 746) / (480 X 0.9 X 0.8 X 1.732) | I = (HP X 746) / (E X EFF X PF X 1.732) | P | 13.99 | 40
13 | Amps from KW | 4.5107 | 4.51 = (3 X 1000) / (480 X 0.8 X 1.732) | I = (KW X 1000) / (E X PF X 1.732) | R | 15.99 | 50
14 | Amps from KVA | 24.057 | 24.06 = (20 X 1000) / (480 X 1.732) | I = (KVA X 1000) / (E X 1.732) | S | 17.99 | 60
15 | KW | 86.4614 | 86.46 = (480 X 130 X 0.8 X 1.732) / 1000 | KW = (E X I X PF X 1.732) / 1000 | T | 19.99 | 75
16 | KVA | 108.0768 | 108.08 = (480 X 130 X 1.732) / 1000 | KVA = (E X I X 1.732) / 1000 | U | 22.39 | 100
17 | HP | 104.31 | 104.31 = (480 X 130 X 0.9 X 0.8 X 1.732) / 746 | HP = (E x I x EFF x PF x 1.732) / 746 | V | 22.4 | 125
18 | Locked Rotor Current | 1080.1578 | 1080.16 = (200 X 4.49 X 1000) / (480 X 1.732) | LRC = (HP X KVA/HP X 1000) / (E X 1.732) | LR CODE | MULT | 150
19 |  |  |  |  | D | 4.49 | 200
20 | Single Phase |  | Single Phase Calculation | Single Phase Formula |  |  | 250
21 | Amps from HP | 431.713 | 431.71 = (200 X 746) / (480 X 0.9 X 0.8) | I = (HP X 746) / (E X EFF X PF) |  |  | 300
22 | Amps from KW | 7.8125 | 7.81 = (3 X 1000) / (480 X 0.8) | I = (KW X 1000) / (E X PF) |  |  | 350
23 | Amps from KVA | 41.6667 | 41.67 = (20 X 1000) / 480 | I = (KVA X 1000) / E |  |  | 400
24 | KW | 49.92 | 49.92 = (480 X 130 X 0.8) / 1000 | KW = (E X I X PF) / 1000 |  |  | 450
25 | KVA | 62.4 | 62.4 = (480 X 130) / 1000 | KVA = (E X I) / 1000 |  |  | 500
26 | HP | 60.2252 | 60.23 = (480 X 130 X 0.9 X 0.8) / 746 | HP = (E X I X EFF X PF) / 746 |  |  | 600
27 | Locked Rotor Current | 1870.8333 | 1870.83 = (200 X 4.49 X 1000) / 480 | LRC = (HP X KVA/HP X 1000) / E |  |  | 700
28 | [6 empty] | 800
29 | DC |  | DC Calculation | DC Formula |  |  | 900
30 | Amps from HP | 345.3704 | 345.37 = (200 X 746) / (480 X 0.9) | I = (HP X 746) / (E X EFF) |  |  | 1000
31 | Amps from KW | 6.25 | 6.25 = (3 X 1000) / 480 | I = (KW X 1000) / E |  |  | 1250
32 | KW | 62.4 | 62.4 = (480 X 130) / 1000 | KW = (E X I) / 1000 |  |  | 1500
33 | HP | 75.2815 | 75.28 = (480 X 130 X 0.9) / 746 | HP = (E X I X EFF) / 746 |  |  | 1750
2000
Spreadsheet by: | [6 empty] | 2250
Lorn Macilravie, Master Electrician | [6 empty] | 2500
risingedgeservices@gmail.com | [6 empty] | 2750
Mobile: 307-696-7926
The YELLOW cells are not protected.

## Quick S.C.
Quick Three Phase Short Circuit Calculator
1500 | Transformer Bank KVA
480 | Volts, Line to Line
1804.2725 | Transformer Full Load Amps (FLA)
3.5% | Z, Transformer Impedance
51550.6434 | Available Amps Short Circuit, I s.c.
52 | kA
1804.2725 | 3 Phase Transformer FLA = KVA X 1000 / E L-L X 1.73
28.5714 | "M" Multiplier = 100 / % Z
51550.6434 | Transformer let thru Short Circuit current = Transformer FLA X M
28.5714 | Isc/IL, for IEEE 519
3125 | Single Phase Transformer FLA = KVA X 1000 / E L-L
Spreadsheet by:
Lorn MacIlravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## PD Pumps
Positive Displacement Pump Calculation
60 | Stroke Length (Inches)
1.5 | Bore Diameter (Inches)
1 | Pistons (Use "1" for Rod Pumps) (Use "3" for a Triplex)
5 | RPM, or SPM
0.75 | Radius (Bore/2)
3.1416 | Pi
1.7671 | Sq. Inches of Circle (Radius x Radius x Pi)
106.0288 | Cubic Inches Per Stroke (Stroke Length x Sq. Inches of Circle)
106.0288 | Cubic Inches Per Revolution (Cubic Inches Per Stroke x No. of Pistons)
0.459 | Gallons per Revolution (Cubic Inches Per Revolution /231)
2.295 | U.S. Gallons per Minute
3304.7923 | U.S. Gallons per Day
78.6855 | BPD at 100% Eff.
90% | Efficiency
70.817 | BPD x Eff.
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## 460 Motors
2016-11-15
460 VOLT – THREE PHASE - MOTOR CALCULATIONS
HP | KW | NEC AMPS | 125% | 175% | 250% | TD FUSE | ITB | FUSED DIS. SIZE | NEMA SIZE | THHN | AREA | EQUIP. GRND | AREA | TOTAL AREA | MIN. RMC | MIN. EYS
½ | 0.373 | 1.1 | 1.375 | 1.925 | 2.75 | 3 | 3 | 30 | OO | 14 | 0.0097 | 14 | 0.0097 | 0.0388 | ½ | ½
¾ | 0.5595 | 1.6 | 2 | 2.8 | 4 | 3 | 6 | 30 | OO | 14 | 0.0097 | 14 | 0.0097 | 0.0388 | ½ | ½
1 | 0.746 | 2.1 | 2.625 | 3.675 | 5.25 | 6 | 6 | 30 | OO | 14 | 0.0097 | 14 | 0.0097 | 0.0388 | ½ | ½
1 ½ | 1.119 | 3 | 3.75 | 5.25 | 7.5 | 6 | 10 | 30 | OO | 14 | 0.0097 | 14 | 0.0097 | 0.0388 | ½ | ½
2 | 1.492 | 3.4 | 4.25 | 5.95 | 8.5 | 6 | 10 | 30 | OO | 14 | 0.0097 | 14 | 0.0097 | 0.0388 | ½ | ½
3 | 2.238 | 4.8 | 6 | 8.4 | 12 | 10 | 15 | 30 | O | 14 | 0.0097 | 14 | 0.0097 | 0.0388 | ½ | ½
5 | 3.73 | 7.6 | 9.5 | 13.3 | 19 | 15 | 20 | 30 | O | 14 | 0.0097 | 14 | 0.0097 | 0.0388 | ½ | ½
7 ½ | 5.595 | 11 | 13.75 | 19.25 | 27.5 | 20 | 30 | 30 | 1 | 14 | 0.0097 | 14 | 0.0097 | 0.0388 | ½ | ½
10 | 7.46 | 14 | 17.5 | 24.5 | 35 | 25 | 40 | 30 | 1 | 12 | 0.0133 | 12 | 0.0097 | 0.0496 | ½ | ½
15 | 11.19 | 21 | 26.25 | 36.75 | 52.5 | 40 | 60 | 60 | 2 | 10 | 0.0211 | 12 | 0.0133 | 0.0766 | ½ | ½
20 | 14.92 | 27 | 33.75 | 47.25 | 67.5 | 50 | 70 | 60 | 2 | 8 | 0.0366 | 10 | 0.0211 | 0.1309 | ¾ | ¾
25 | 18.65 | 34 | 42.5 | 59.5 | 85 | 60 | 90 | 60 | 2 | 6 | 0.0507 | 10 | 0.0211 | 0.1732 | ¾ | 1
30 | 22.38 | 40 | 50 | 70 | 100 | 70 | 100 | 100 | 3 | 6 | 0.0507 | 8 | 0.0366 | 0.1887 | ¾ | 1
40 | 29.84 | 52 | 65 | 91 | 130 | 100 | 150 | 100 | 3 | 4 | 0.0824 | 8 | 0.0366 | 0.2838 | 1 | 1 ¼
50 | 37.3 | 65 | 81.25 | 113.75 | 162.5 | 125 | 175 | 200 | 3 | 3 | 0.0973 | 6 | 0.0507 | 0.3426 | 1 | 1 ¼
60 | 44.76 | 77 | 96.25 | 134.75 | 192.5 | 150 | 200 | 200 | 4 | 1 | 0.1562 | 6 | 0.0507 | 0.5193 | 1 ¼ | 2
75 | 55.95 | 96 | 120 | 168 | 240 | 175 | 250 | 200 | 4 | 1 | 0.1562 | 6 | 0.0507 | 0.5193 | 1 ¼ | 2
100 | 74.6 | 124 | 155 | 217 | 310 | 225 | 350 | 400 | 4 | 2/O | 0.2223 | 4 | 0.0824 | 0.7493 | 1 ½ | 2
125 | 93.25 | 156 | 195 | 273 | 390 | 300 | 400 | 400 | 5 | 3/O | 0.2679 | 4 | 0.0824 | 0.8861 | 2 | 2 ½
150 | 111.9 | 180 | 225 | 315 | 450 | 350 | 450 | 400 | 5 | 4/O | 0.3237 | 3 | 0.0973 | 1.0684 | 2 | 2 ½
200 | 149.2 | 240 | 300 | 420 | 600 | 450 | 600 | 600 | 5 | 350 | 0.5242 | 2 | 0.1158 | 1.6884 | 2 ½ | 3
250 | 186.5 | 302 | 377.5 | 528.5 | 755 | 600 | 800 | 600 | 6 | 500 | 0.7073 | 1 | 0.1562 | 2.2781 | 3 | 3 ½
300 | 223.8 | 361 | 451.25 | 631.75 | 902.5 | 700 | 1000 | 800 | 6 | 700 | 0.9887 | 1/O | 0.1855 | 3.1516 | 3 ½ | 4
350 | 261.1 | 414 | 517.5 | 724.5 | 1035 | 800 | 1200 | 800 | 6 | 900 | 1.2311 | 1/O | 0.1855 | 3.8788 | 3 ½ | 5
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
307-696-7926
The YELLOW cells are not protected.
Note on K3: Lorn Macilravie: See 110.14(C)(1)(a). Any wire size over 100A in this chart is chosen from the 75C column. Any wire under 100A is chosen from the 60C column.
Note on M3: Lorn Macilravie: Equipment ground size is based on the TD Fuse size. See Table 250.122
Note on K20: Lorn Macilravie: See 110.14(C)(1)(a). Any wire size over 100A in this chart is chosen from the 75C column.

## 460 Motors 2X
2016-11-15
460 VOLT – THREE PHASE - MOTOR CALCULATIONS FOR PARALLEL RUNS
HP | KW | NEC AMPS | 125% | 175% | 250% | D/2 | TD FUSE | ITB | FUSED DIS. SIZE | NEMA SIZE | THHN X2 | AREA | EQUIP. GRND X2 | AREA | TOTAL AREA | MIN. RMC X2 | MIN. EYS X2
200 | 149.2 | 240 | 300 | 420 | 600 | 150 | 450 | 600 | 600 | 5 | 1/O | 0.1855 | 2 | 0.1158 | 0.6723 | 1.5 | 2
250 | 186.5 | 302 | 377.5 | 528.5 | 755 | 188.75 | 600 | 800 | 600 | 6 | 3/O | 0.2679 | 1 | 0.1562 | 0.9599 | 2 | 2.5
300 | 223.8 | 361 | 451.25 | 631.75 | 902.5 | 225.625 | 700 | 1000 | 800 | 6 | 4/O | 0.3237 | 1/O | 0.1855 | 1.1566 | 2 | 2.5
350 | 261.1 | 414 | 517.5 | 724.5 | 1035 | 258.75 | 800 | 1200 | 800 | 6 | 300 | 0.4608 | 1/O | 0.1855 | 1.5679 | 2.5 | 3
400 | 298.4 | 477 | 596.25 | 834.75 | 1192.5 | 500 | 1000 | 1200 | 1200 | 6 | 900 | 1.2311 | 2/O | 0.2223 | 3.9156 | 3.5 | 5
450 | 335.7 | 515 | 643.75 | 901.25 | 1287.5 | 500 | 1000 | 1600 | 1200 | 7 | 900 | 1.2311 | 2/O | 0.2223 | 3.9156 | 3.5 | 5
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
307-696-7926
The YELLOW cells are not protected.
Note on L3: Lorn Macilravie: See 110.14(C)(1)(a). Any wire size over 100A in this chart is chosen from the 75C column. Any wire under 100A is chosen from the 60C column.
Note on N3: Lorn Macilravie: 250.122(F)
Note on O3: Lorn Macilravie: Based on TD Fuse Size
Note on L8: Lorn Macilravie: 240.4(C)
Note on L9: Lorn Macilravie: 240.4(C)

## Single Phase Motors
115 VOLT – SINGLE PHASE - MOTOR CALCULATIONS - FROM TABLE 430.248
HP | KW | NEC AMPS | 125% | 1.75 | TD FUSE | FUSED DIS. SIZE | NEMA SIZE | THHN | AREA | EQUIP. GRND | AREA | TOTAL AREA | MIN. RMC | MIN. EYS
1/6 | 0.12433 | 4.4 | 5.5 | 7.7 | 10 | 30 | OO | 14 | 0.0097 | 14 | 0.0097 | 0.0291 | 1/2 | 1/2
1/4 | 0.1865 | 5.8 | 7.25 | 10.15 | 15 | 30 | OO | 14 | 0.0097 | 14 | 0.0097 | 0.0291 | 1/2 | 1/2
1/3 | 0.24867 | 7.2 | 9 | 12.6 | 15 | 30 | OO | 14 | 0.0097 | 14 | 0.0097 | 0.0291 | 1/2 | 1/2
½ | 0.373 | 9.8 | 12.25 | 17.15 | 20 | 30 | O | 14 | 0.0097 | 12 | 0.0133 | 0.0327 | 1/2 | 1/2
¾ | 0.5595 | 13.8 | 17.25 | 24.15 | 25 | 30 | O | 12 | 0.0133 | 12 | 0.0133 | 0.0399 | 1/2 | 1/2
1 | 0.746 | 16 | 20 | 28 | 30 | 30 | O | 12 | 0.0133 | 12 | 0.0133 | 0.0399 | 1/2 | 1/2
1 ½ | 1.119 | 20 | 25 | 35 | 35 | 60 | 1 | 10 | 0.0211 | 10 | 0.0211 | 0.0633 | 1/2 | 1/2
2 | 1.492 | 24 | 30 | 42 | 45 | 60 | 1 | 10 | 0.0211 | 10 | 0.0211 | 0.0633 | 1/2 | 1/2
3 | 2.238 | 34 | 42.5 | 59.5 | 60 | 60 | 2 | 6 | 0.0507 | 10 | 0.0211 | 0.1225 | 1/2 | 3/4
5 | 3.73 | 56 | 70 | 98 | 100 | 100 | 3 | 4 | 0.0824 | 8 | 0.0366 | 0.2014 | 3/4 | 1
7 ½ | 5.595 | 80 | 100 | 140 | 150 | 200 | 3 | 1 | 0.1562 | 6 | 0.0507 | 0.3631 | 1 - 1/4" | 1 - 1/4"
10 | 7.46 | 100 | 125 | 175 | 175 | 200 | 4 | 1/O | 0.1855 | 6 | 0.0507 | 0.4217 | 1 - 1/4" | 1 - 1/2"
208 VOLT – SINGLE PHASE - MOTOR CALCULATIONS - FROM TABLE 430.248
HP | KW | NEC AMPS | 125% | 1.75 | TD FUSE | FUSED DIS. SIZE | NEMA SIZE | THHN | AREA | EQUIP. GRND | AREA | TOTAL AREA | MIN. RMC | MIN. EYS
1/6 | 0.12433 | 2.4 | 3 | 4.2 | 6 | 30 | OO | 14 | 0.0097 | 14 | 0.0097 | 0.0291 | 1/2 | 1/2
1/4 | 0.1865 | 3.2 | 4 | 5.6 | 6 | 30 | OO | 14 | 0.0097 | 14 | 0.0097 | 0.0291 | 1/2 | 1/2
1/3 | 0.24867 | 4 | 5 | 7 | 10 | 30 | OO | 14 | 0.0097 | 14 | 0.0097 | 0.0291 | 1/2 | 1/2
½ | 0.373 | 5.4 | 6.75 | 9.45 | 10 | 30 | OO | 14 | 0.0097 | 14 | 0.0097 | 0.0291 | 1/2 | 1/2
¾ | 0.5595 | 7.6 | 9.5 | 13.3 | 15 | 30 | OO | 14 | 0.0097 | 14 | 0.0097 | 0.0291 | 1/2 | 1/2
1 | 0.746 | 8.8 | 11 | 15.4 | 20 | 30 | OO | 14 | 0.0097 | 14 | 0.0097 | 0.0291 | 1/2 | 1/2
1 ½ | 1.119 | 11 | 13.75 | 19.25 | 20 | 30 | O | 14 | 0.0097 | 14 | 0.0097 | 0.0291 | 1/2 | 1/2
2 | 1.492 | 13.2 | 16.5 | 23.1 | 25 | 30 | O | 12 | 0.0133 | 12 | 0.0133 | 0.0399 | 1/2 | 1/2
3 | 2.238 | 18.7 | 23.375 | 32.725 | 35 | 60 | 1 | 10 | 0.0211 | 10 | 0.0211 | 0.0633 | 1/2 | 1/2
5 | 3.73 | 30.8 | 38.5 | 53.9 | 60 | 60 | 2 | 8 | 0.0366 | 10 | 0.0211 | 0.0943 | 1/2 | 3/4
7 ½ | 5.595 | 44 | 55 | 77 | 80 | 100 | 2 | 6 | 0.0507 | 8 | 0.0366 | 0.138 | 3/4 | 1
10 | 7.46 | 55 | 68.75 | 96.25 | 100 | 100 | 3 | 4 | 0.0824 | 8 | 0.0366 | 0.2014 | 3/4 | 1
230 VOLT – SINGLE PHASE - MOTOR CALCULATIONS - FROM TABLE 430.248
HP | KW | NEC AMPS | 125% | 1.75 | TD FUSE | FUSED DIS. SIZE | NEMA SIZE | THHN | AREA | EQUIP. GRND | AREA | TOTAL AREA | MIN. RMC | MIN. EYS
1/6 | 0.12433 | 2.2 | 2.75 | 3.85 | 6 | 30 | OO | 14 | 0.0097 | 14 | 0.0097 | 0.0291 | 1/2 | 1/2
1/4 | 0.1865 | 2.9 | 3.625 | 5.075 | 6 | 30 | OO | 14 | 0.0097 | 14 | 0.0097 | 0.0291 | 1/2 | 1/2
1/3 | 0.24867 | 3.6 | 4.5 | 6.3 | 10 | 30 | OO | 14 | 0.0097 | 14 | 0.0097 | 0.0291 | 1/2 | 1/2
½ | 0.373 | 4.9 | 6.125 | 8.575 | 10 | 30 | OO | 14 | 0.0097 | 14 | 0.0097 | 0.0291 | 1/2 | 1/2
¾ | 0.5595 | 6.9 | 8.625 | 12.075 | 15 | 30 | OO | 14 | 0.0097 | 14 | 0.0097 | 0.0291 | 1/2 | 1/2
1 | 0.746 | 8 | 10 | 14 | 15 | 30 | OO | 14 | 0.0097 | 14 | 0.0097 | 0.0291 | 1/2 | 1/2
1 ½ | 1.119 | 10 | 12.5 | 17.5 | 20 | 30 | O | 14 | 0.0097 | 12 | 0.0133 | 0.0327 | 1/2 | 1/2
2 | 1.492 | 12 | 15 | 21 | 25 | 30 | O | 14 | 0.0097 | 10 | 0.0211 | 0.0405 | 1/2 | 1/2
3 | 2.238 | 17 | 21.25 | 29.75 | 30 | 30 | O | 10 | 0.0211 | 10 | 0.0211 | 0.0633 | 1/2 | 1/2
5 | 3.73 | 28 | 35 | 49 | 50 | 60 | 1 | 8 | 0.0366 | 10 | 0.0211 | 0.0943 | 1/2 | 3/4
7 ½ | 5.595 | 40 | 50 | 70 | 70 | 100 | 1 | 6 | 0.0507 | 8 | 0.0366 | 0.138 | 3/4 | 1
10 | 7.46 | 50 | 62.5 | 87.5 | 90 | 200 | 2 | 4 | 0.0824 | 8 | 0.0366 | 0.2014 | 3/4 | 1
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
307-696-7926
The YELLOW cells are not protected.
Note on I4: Lorn Macilravie: See 110.14(C)(1)
Note on I19: Lorn Macilravie: See 110.14(C)(1)
Note on I34: Lorn Macilravie: See 110.14(C)(1)

## Conduit Fill
Conductor Fill Calculator |  |  |  |  | 2016-11-15
LINE | QTY | WIRE | IN2 | TOTAL AREA
1 | 5 | # 14 THHN | 0.0097 | 0.0485
2 | 7 | # 12 THHN | 0.0133 | 0.0931
3 | 5 | # 10 THHN | 0.0211 | 0.1055
4 | 4 | #8 THHN | 0.0366 | 0.1464
5 | 0 | #6 THHN | 0.0507 | 0
6 | 0 | #4 THHN | 0.0824 | 0
7 | 0 | #3 THHN | 0.0973 | 0
8 | 0 | #2 THHN | 0.1158 | 0
9 | 0 | #1 THHN | 0.1562 | 0
10 | 0 | 1/O THHN | 0.1855 | 0
11 | 0 | 2/O THHN | 0.2223 | 0
12 | 0 | 3/O THHN | 0.2679 | 0
13 | 0 | 4/O THHN | 0.3237 | 0
14 | 0 | 250 THHN | 0.397 | 0
15 | 0 | 300 THHN | 0.4608 | 0
16 | 0 | 350 THHN | 0.5242 | 0
17 | 0 | 400 THHN | 0.5863 | 0
18 | 0 | 500 THHN | 0.7073 | 0
19 | 0 | 600 THHN | 0.8676 | 0
20 | 0 | 700 THHN | 0.9887 | 0
21 | 0 | 750 THHN | 1.0496 | 0
22 | 0 | 800 THHN | 1.1085 | 0
23 | 0 | 900 THHN | 1.2311 | 0
24 | 0 | 1000 THHN | 1.3478 | 0
25 |  |  |  | 0.3935 | Subtotal 1
26 |  | CABLE DIA.
27 | QTY | "INCHES" | IN2 | TOTAL AREA
28 | 0 | 0.5 | 0.19625 | 0
29 | 0 | 2 | 3.14 | 0
30 | 0 | 2 | 3.14 | 0
31 |  |  |  |  | Other
32 |  |  |  |  | Other
33 |  |  |  | 0 | Subtotal 2
34
35 |  |  |  | 0.3935 | Subtotal 1
36 |  |  |  | 0 | Subtotal 2 | +
37 |  |  |  | 0.3935 | Total Wire Fill
Notes:
1 | Add up the total area of your conductor fill.
a. Look up your wire and wire area (IN2) in Chapter 9, Table 5.
b. Calculate the area of individual cables. Use the formula, πr2
2 | Choose your conduit size from Chapter 9, Table 4
| a. | Use 60% fill for conduits 24" or less, NEC Note to Ch. 9, Table 1.
| b. | Use 53% fill for single wires and single cables, NEC Ch. 9, Table 1.
| c. | Use 40% fill for most conduit applications, NEC Ch. 9, Table 1.
| d. | Use 31% fill for two wire applications, NEC Ch. 9, Table 1.
| e. | Use 25% fill for seal off (EYS) fittings, NEC 501.15
| f. | Use 20% fill for wireways, NEC 376.22(A)
Rigid Metal Conduit (RMC) - Area in IN2
TRADE | TOTAL AREA | < 24" Nipple | 1 WIRE | 2 WIRE | OVER 2 WIRES | SEAL OFF
SIZE | 100% | 60% | 53% | 31% | 40% | 25%
1/2" | 0.314 | 0.1884 | 0.16642 | 0.09734 | 0.1256 | 0.0785
3/4" | 0.549 | 0.3294 | 0.29097 | 0.17019 | 0.2196 | 0.13725
1" | 0.887 | 0.5322 | 0.47011 | 0.27497 | 0.3548 | 0.22175
1 - 1/4" | 1.526 | 0.9156 | 0.80878 | 0.47306 | 0.6104 | 0.3815
1 - 1/2" | 2.071 | 1.2426 | 1.0976 | 0.64201 | 0.8284 | 0.51775
2" | 3.408 | 2.0448 | 1.8062 | 1.0565 | 1.3632 | 0.852
2 - 1/2" | 4.866 | 2.9196 | 2.579 | 1.5085 | 1.9464 | 1.2165
3" | 7.499 | 4.4994 | 3.9745 | 2.3247 | 2.9996 | 1.8747
3 - 1/2" | 10.01 | 6.006 | 5.3053 | 3.1031 | 4.004 | 2.5025
4" | 12.882 | 7.7292 | 6.8275 | 3.9934 | 5.1528 | 3.2205
5" | 20.212 | 12.1272 | 10.7124 | 6.2657 | 8.0848 | 5.053
6" | 29.158 | 17.4948 | 15.4537 | 9.039 | 11.6632 | 7.2895
Rigid PVC, Schedule 40- Area in IN2
TRADE | TOTAL AREA | < 24" Nipple | 1 WIRE | 2 WIRE | OVER 2 WIRES | SEAL OFF
SIZE | 100% | 60% | 53% | 31% | 40% | 25%
1/2" | 0.285 | 0.171 | 0.15105 | 0.08835 | 0.114 | 0.07125
3/4" | 0.508 | 0.3048 | 0.26924 | 0.15748 | 0.2032 | 0.127
1" | 0.832 | 0.4992 | 0.44096 | 0.25792 | 0.3328 | 0.208
1 - 1/4" | 1.453 | 0.8718 | 0.77009 | 0.45043 | 0.5812 | 0.36325
1 - 1/2" | 1.986 | 1.1916 | 1.0526 | 0.61566 | 0.7944 | 0.4965
2" | 3.291 | 1.9746 | 1.7442 | 1.0202 | 1.3164 | 0.82275
2 - 1/2" | 4.695 | 2.817 | 2.4884 | 1.4555 | 1.878 | 1.1738
3" | 7.268 | 4.3608 | 3.852 | 2.2531 | 2.9072 | 1.817
3 - 1/2" | 9.737 | 5.8422 | 5.1606 | 3.0185 | 3.8948 | 2.4343
4" | 12.554 | 7.5324 | 6.6536 | 3.8917 | 5.0216 | 3.1385
5" | 19.761 | 11.8566 | 10.4733 | 6.1259 | 7.9044 | 4.9402
6" | 28.567 | 17.1402 | 15.1405 | 8.8558 | 11.4268 | 7.1418
EMT - Area in IN2
TRADE | TOTAL AREA | < 24" Nipple | 1 WIRE | 2 WIRE | OVER 2 WIRES | SEAL OFF
SIZE | 100% | 60% | 53% | 31% | 40% | 25%
1/2" | 0.304 | 0.1824 | 0.16112 | 0.09424 | 0.1216 | 0.076
3/4" | 0.533 | 0.3198 | 0.28249 | 0.16523 | 0.2132 | 0.13325
1" | 0.864 | 0.5184 | 0.45792 | 0.26784 | 0.3456 | 0.216
1 - 1/4" | 1.496 | 0.8976 | 0.79288 | 0.46376 | 0.5984 | 0.374
1 - 1/2" | 2.036 | 1.2216 | 1.0791 | 0.63116 | 0.8144 | 0.509
2" | 3.356 | 2.0136 | 1.7787 | 1.0404 | 1.3424 | 0.839
2 - 1/2" | 5.858 | 3.5148 | 3.1047 | 1.816 | 2.3432 | 1.4645
3" | 8.846 | 5.3076 | 4.6884 | 2.7423 | 3.5384 | 2.2115
3 - 1/2" | 11.545 | 6.927 | 6.1189 | 3.5789 | 4.618 | 2.8862
4" | 14.753 | 8.8518 | 7.8191 | 4.5734 | 5.9012 | 3.6883
Liquidtight (LFMC) - Area in IN2
TRADE | TOTAL AREA | < 24" Nipple | 1 WIRE | 2 WIRE | OVER 2 WIRES | SEAL OFF
SIZE | 100% | 60% | 53% | 31% | 40% | 25%
1/2" | 0.314 | 0.1884 | 0.16642 | 0.09734 | 0.1256 | 0.0785
3/4" | 0.541 | 0.3246 | 0.28673 | 0.16771 | 0.2164 | 0.13525
1" | 0.873 | 0.5238 | 0.46269 | 0.27063 | 0.3492 | 0.21825
1 - 1/4" | 1.528 | 0.9168 | 0.80984 | 0.47368 | 0.6112 | 0.382
1 - 1/2" | 1.981 | 1.1886 | 1.0499 | 0.61411 | 0.7924 | 0.49525
2" | 3.246 | 1.9476 | 1.7204 | 1.0063 | 1.2984 | 0.8115
2 - 1/2" | 4.881 | 2.9286 | 2.5869 | 1.5131 | 1.9524 | 1.2203
3" | 7.475 | 4.485 | 3.9617 | 2.3173 | 2.99 | 1.8687
3 - 1/2" | 9.731 | 5.8386 | 5.1574 | 3.0166 | 3.8924 | 2.4327
4" | 12.692 | 7.6152 | 6.7268 | 3.9345 | 5.0768 | 3.173
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
307-696-7926
The YELLOW cells are not protected.

## Wire Size
Wire Sizing, with Temperature and Fill Adjustments | [7 empty] | 2016-11-20 | [5 empty] | Table 310.15(B)(3)(a) Adjustment for Number of Conductors | 0.5
See 110.14(C), 210.19 (A)(1), 215.2(A), 430.22 and 430.24 | [13 empty] | Table 310.15(B)(2)(a) Temperature Adjustment | 0.71 | X | Table 310.15(B)(3)(a) Adjustment for No. Conductors
[14 empty] | Total Adjustment | 0.355
| Description | Continuous Load | Amps | Mult. | Totals | Min. AWG | AWG | No. of CCC | [8 empty] | No. of Cond. | Multiplier
LINE |  | Noncontinuous Load | [6 empty] | Table 310.15(B)(3)(a) Adjusted for Temp. and No. of Conductors in the Conduit by a Mult. of 0.355 | [7 empty] | 4-6 | 0.8
1 | 20 HP Motor | Continuous Load | 27 | 1.25 | 33.75 | 8 | 4 | 3 |  | CU |  |  | AL |  |  |  | 7-9 | 0.7
2 | 20 HP Motor | Continuous Load | 27 | 1.25 | 33.75 | 8 | 4 | 3 | AWG | 60C | 75C | 90C | 60C | 75C | 90C | AWG | 10-20 | 0.5
3 | 15 HP Motor | Continuous Load | 21 | 1.25 | 26.25 | 10 | 6 | 3 | 14 | 5.325 | 7.1 | 8.875 | -- | -- | -- | 14 | 21-30 | 0.45
4 | 15 HP Motor | Continuous Load | 21 | 1.25 | 26.25 | 10 | 6 | 3 | 12 | 7.1 | 8.875 | 10.65 | 5.325 | 7.1 | 8.875 | 12 | 31-40 | 0.4
5 | 10 HP Motor | Continuous Load | 14 | 1.25 | 17.5 | 12 | 8 | 3 | 10 | 10.65 | 12.425 | 14.2 | 8.875 | 10.65 | 12.425 | 10 | >41 | 0.35
6 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 8 | 14.2 | 17.75 | 19.525 | 12.425 | 14.2 | 15.975 | 8
7 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 6 | 19.525 | 23.075 | 26.625 | 14.2 | 17.75 | 19.525 | 6
8 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 4 | 24.85 | 30.175 | 33.725 | 19.525 | 23.075 | 26.625 | 4 | Table 310.15(B)(2)(a) Temperature Adjustment
9 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 3 | 30.175 | 35.5 | 40.825 | 23.075 | 26.625 | 30.175 | 3
10 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 2 | 33.725 | 40.825 | 46.15 | 26.625 | 31.95 | 35.5 | 2 | DEG F | 60C | 75C | 90C
11 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 1 | 39.05 | 46.15 | 51.475 | 30.175 | 35.5 | 40.825 | 1 | <50 | 1.29 | 1.2 | 1.15
12 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 1/O | 44.375 | 53.25 | 60.35 | 35.5 | 42.6 | 47.925 | 1/O | 51-59 | 1.22 | 1.15 | 1.12
13 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 2/O | 51.475 | 62.125 | 69.225 | 40.825 | 47.925 | 53.25 | 2/O | 60-68 | 1.115 | 1.11 | 1.08
14 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 3/O | 58.575 | 71 | 79.875 | 46.15 | 55.025 | 62.125 | 3/O | 69-77 | 1.08 | 1.05 | 10.4
15 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 4/O | 69.225 | 81.65 | 92.3 | 53.25 | 63.9 | 72.775 | 4/O | 78-86 | 1 | 1 | 1
16 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 250 | 76.325 | 90.525 | 102.95 | 60.35 | 72.775 | 81.65 | 250 | 87-95 | 0.91 | 0.94 | 0.96
17 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 300 | 85.2 | 101.175 | 113.6 | 69.225 | 81.65 | 92.3 | 300 | 96-104 | 0.82 | 0.88 | 0.91
18 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 350 | 92.3 | 110.05 | 124.25 | 74.55 | 88.75 | 99.4 | 350 | 105-113 | 0.71 | 0.82 | 0.87
19 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 400 | 99.4 | 118.925 | 134.9 | 79.875 | 95.85 | 108.275 | 400 | 114-122 | 0.58 | 0.75 | 0.82
20 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 500 | 113.6 | 134.9 | 152.65 | 92.3 | 110.05 | 124.25 | 500 | 123-131 | 0.41 | 0.67 | 0.76
21 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 600 | 124.25 | 149.1 | 168.625 | 101.175 | 120.7 | 136.675 | 600 | 132-140 |  | 0.58 | 0.71
22 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 700 | 136.675 | 163.3 | 184.6 | 111.825 | 133.125 | 150.875 | 700 | 141-149 |  | 0.47 | 0.65
23 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 750 | 142 | 168.625 | 189.925 | 113.6 | 136.675 | 154.425 | 750 | 150-158 |  | 0.33 | 0.58
24 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | [8 empty] | 159-167 |  |  | 0.5
25 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | Table 310.15 (B)(16) | [7 empty] | 168-176 |  |  | 0.41
26 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 |  | CU |  |  | AL |  |  |  | 177-185 |  |  | 0.29
27 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | AWG | 60C | 75C | 90C | 60C | 75C | 90C | AWG
28 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 14 | 15 | 20 | 25 | -- | -- | -- | 14
29 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 12 | 20 | 25 | 30 | 15 | 20 | 25 | 12 | See 240.6(A)
30 |  | Noncontinuous Load | 0 | 1 | 0 | None | None | 0 | 10 | 30 | 35 | 40 | 25 | 30 | 35 | 10 | STANDARD OC
[8 empty] | 15 | 8 | 40 | 50 | 55 | 35 | 40 | 45 | 8 | 1 | 175
[8 empty] | Total | 6 | 55 | 65 | 75 | 40 | 50 | 55 | 6 | 3 | 200
Note 1: | [8 empty] | 4 | 70 | 85 | 95 | 55 | 65 | 75 | 4 | 6 | 225
No temperature correction needed. No derating for number of current carrying conductors in the conduit is needed. The equipment is inside a temperature controlled building. | [8 empty] | 3 | 85 | 100 | 115 | 65 | 75 | 85 | 3 | 10 | 250
[9 empty] | 2 | 95 | 115 | 130 | 75 | 90 | 100 | 2 | 15 | 300
[9 empty] | 1 | 110 | 130 | 145 | 85 | 100 | 115 | 1 | 20 | 350
[9 empty] | 1/O | 125 | 150 | 170 | 100 | 120 | 135 | 1/O | 25 | 400
[9 empty] | 2/O | 145 | 175 | 195 | 115 | 135 | 150 | 2/O | 30 | 450
Note 2: | [8 empty] | 3/O | 165 | 200 | 225 | 130 | 155 | 175 | 3/O | 35 | 500
There are a total of 15 current carrying conductors in the conduit. Per Table 310.15(B)(3)(a), Table 310.15(B)(3)(a) needs to be derated by 0.50. It would probably be advisable to run some of these 15 conductors in separate conduits to reduce the wire cost in this installation. | [8 empty] | 4/O | 195 | 230 | 260 | 150 | 180 | 205 | 4/O | 40 | 600
[9 empty] | 250 | 215 | 255 | 290 | 170 | 205 | 230 | 250 | 45 | 700
[9 empty] | 300 | 240 | 285 | 320 | 195 | 230 | 260 | 300 | 50 | 800
[9 empty] | 350 | 260 | 310 | 350 | 210 | 250 | 280 | 350 | 60 | 1000
[9 empty] | 400 | 280 | 335 | 380 | 225 | 270 | 305 | 400 | 70 | 1200
Note 3: | [8 empty] | 500 | 320 | 380 | 430 | 260 | 310 | 350 | 500 | 80 | 1600
[9 empty] | 600 | 350 | 420 | 475 | 285 | 340 | 385 | 600 | 90 | 2000
[9 empty] | 700 | 385 | 460 | 520 | 315 | 375 | 425 | 700 | 100 | 2500
[9 empty] | 750 | 400 | 475 | 535 | 320 | 385 | 435 | 750 | 110 | 3000
[9 empty] | None | [7 empty] | 125 | 4000
[9 empty] | Spreadsheet by: | [7 empty] | 150 | 5000
Lorn Macilravie, Master Electrician, 307-696-7926, risingedgeservices@gmail.com
Spreadsheet by: | [8 empty] | For occasional spreadsheet updates, go to: https://sites.google.com/site/macilravie/
Lorn Macilravie, Master Electrician, 307-696-7926, risingedgeservices@gmail.com | [8 empty] | The YELLOW cells are not protected.
For occasional spreadsheet updates, go to: https://sites.google.com/site/macilravie/
The YELLOW cells are not protected.
Note on G4: Lorn: Based on 310.15(B)(3)(a) and 110.14(C).
Note on H4: Lorn: Choose wire size from the "adjusted" table.

## Feeder
Feeder Sizing, with Temperature and Fill Adjustments | [5 empty] | 2016-11-20 | [5 empty] | Table 310.15(B)(3)(a) Adjustment for Number of Conductors | 0.8
See 110.14(C), 210.19 (A)(1), 215.2(A), 430.22 and 430.24 | [11 empty] | Table 310.15(B)(2)(a) Temperature Adjustment | 0.94 | X | Table 310.15(B)(3)(a) Adjustment for No. Conductors
[12 empty] | Total Adjustment | 0.752
| Description | Largest Motor | Amps | Mult. | Totals | Note | [8 empty] | No. of Cond. | Multiplier
|  | FLC, Other Motor |  |  |  |  | Table 310.15(B)(3)(a) Adjusted for Temp. and No. of Conductors in the Conduit by a Mult. of 0.752 | [7 empty] | 4-6 | 0.8
|  | Continuous Load | [5 empty] | CU |  |  | AL |  |  |  | 7-9 | 0.7
LINE |  | Noncontinuous Load |  |  |  |  | AWG | 60C | 75C | 90C | 60C | 75C | 90C | AWG | 10-20 | 0.5
1 | 20 HP Motor | Largest Motor | 27 | 1.25 | 33.75 |  | 14 | 11.28 | 15.04 | 18.8 | -- | -- | -- | 14 | 21-30 | 0.45
2 | 20 HP Motor | FLC, Other Motor | 27 | 1 | 27 |  | 12 | 15.04 | 18.8 | 22.56 | 11.28 | 15.04 | 18.8 | 12 | 31-40 | 0.4
3 | 15 HP Motor | FLC, Other Motor | 21 | 1 | 21 |  | 10 | 22.56 | 26.32 | 30.08 | 18.8 | 22.56 | 26.32 | 10 | >41 | 0.35
4 | 15 HP Motor | FLC, Other Motor | 21 | 1 | 21 |  | 8 | 30.08 | 37.6 | 41.36 | 26.32 | 30.08 | 33.84 | 8
5 | 10 HP Motor | FLC, Other Motor | 14 | 1 | 14 |  | 6 | 41.36 | 48.88 | 56.4 | 30.08 | 37.6 | 41.36 | 6
6 |  | Noncontinuous Load | 0 | 1 | 0 |  | 4 | 52.64 | 63.92 | 71.44 | 41.36 | 48.88 | 56.4 | 4 | Table 310.15(B)(2)(a) Temperature Adjustment
7 |  | Continuous Load | 0 | 1.25 | 0 |  | 3 | 63.92 | 75.2 | 86.48 | 48.88 | 56.4 | 63.92 | 3
8 |  | Noncontinuous Load | 0 | 1 | 0 |  | 2 | 71.44 | 86.48 | 97.76 | 56.4 | 67.68 | 75.2 | 2 | DEG F | 60C | 75C | 90C
9 |  | Noncontinuous Load | 0 | 1 | 0 |  | 1 | 82.72 | 97.76 | 109.04 | 63.92 | 75.2 | 86.48 | 1 | <50 | 1.29 | 1.2 | 1.15
10 |  | Noncontinuous Load | 0 | 1 | 0 |  | 1/O | 94 | 112.8 | 127.84 | 75.2 | 90.24 | 101.52 | 1/O | 51-59 | 1.22 | 1.15 | 1.12
11 |  | Noncontinuous Load | 0 | 1 | 0 |  | 2/O | 109.04 | 131.6 | 146.64 | 86.48 | 101.52 | 112.8 | 2/O | 60-68 | 1.115 | 1.11 | 1.08
12 |  | Noncontinuous Load | 0 | 1 | 0 |  | 3/O | 124.08 | 150.4 | 169.2 | 97.76 | 116.56 | 131.6 | 3/O | 69-77 | 1.08 | 1.05 | 10.4
13 |  | Noncontinuous Load | 0 | 1 | 0 |  | 4/O | 146.64 | 172.96 | 195.52 | 112.8 | 135.36 | 154.16 | 4/O | 78-86 | 1 | 1 | 1
14 |  | Noncontinuous Load | 0 | 1 | 0 |  | 250 | 161.68 | 191.76 | 218.08 | 127.84 | 154.16 | 172.96 | 250 | 87-95 | 0.91 | 0.94 | 0.96
15 |  | Noncontinuous Load | 0 | 1 | 0 |  | 300 | 180.48 | 214.32 | 240.64 | 146.64 | 172.96 | 195.52 | 300 | 96-104 | 0.82 | 0.88 | 0.91
16 |  | Noncontinuous Load | 0 | 1 | 0 |  | 350 | 195.52 | 233.12 | 263.2 | 157.92 | 188 | 210.56 | 350 | 105-113 | 0.71 | 0.82 | 0.87
17 |  | Noncontinuous Load | 0 | 1 | 0 |  | 400 | 210.56 | 251.92 | 285.76 | 169.2 | 203.04 | 229.36 | 400 | 114-122 | 0.58 | 0.75 | 0.82
18 |  | Noncontinuous Load | 0 | 1 | 0 |  | 500 | 240.64 | 285.76 | 323.36 | 195.52 | 233.12 | 263.2 | 500 | 123-131 | 0.41 | 0.67 | 0.76
19 |  | Noncontinuous Load | 0 | 1 | 0 |  | 600 | 263.2 | 315.84 | 357.2 | 214.32 | 255.68 | 289.52 | 600 | 132-140 |  | 0.58 | 0.71
20 |  | Noncontinuous Load | 0 | 1 | 0 |  | 700 | 289.52 | 345.92 | 391.04 | 236.88 | 282 | 319.6 | 700 | 141-149 |  | 0.47 | 0.65
21 |  | Noncontinuous Load | 0 | 1 | 0 |  | 750 | 300.8 | 357.2 | 402.32 | 240.64 | 289.52 | 327.12 | 750 | 150-158 |  | 0.33 | 0.58
22 |  | Noncontinuous Load | 0 | 1 | 0 |  | 800 | 308.32 | 368.48 | 417.36 | 248.16 | 297.04 | 334.64 | 800 | 159-167 |  |  | 0.5
23 |  | Noncontinuous Load | 0 | 1 | 0 |  | 900 | 327.12 | 391.04 | 439.92 | 266.96 | 319.6 | 360.96 | 900 | 168-176 |  |  | 0.41
24 |  | Noncontinuous Load | 0 | 1 | 0 |  | 1000 | 342.16 | 409.84 | 462.48 | 282 | 334.64 | 376 | 1000 | 177-185 |  |  | 0.29
25 |  | Noncontinuous Load | 0 | 1 | 0 |  | 1250 | 372.24 | 443.68 | 500.08 | 304.56 | 364.72 | 409.84 | 1250
26 |  | Noncontinuous Load | 0 | 1 | 0 |  | 1500 | 394.8 | 470 | 530.16 | 327.12 | 391.04 | 439.92 | 1500
27 |  | Noncontinuous Load | 0 | 1 | 0 |  | 1750 | 409.84 | 488.8 | 552.72 | 342.16 | 409.84 | 462.48 | 1750 | See 240.6(A)
28 |  | Noncontinuous Load | 0 | 1 | 0 |  | 2000 | 417.36 | 500.08 | 564 | 353.44 | 421.12 | 473.76 | 2000 | STANDARD OC
29 |  | Noncontinuous Load | 0 | 1 | 0 | [9 empty] | 1 | 175
30 |  | Noncontinuous Load | 0 | 1 | 0 |  | Table 310.15 (B)(16) | [7 empty] | 3 | 200
|  |  | 27 |  | 116.75 |  |  | CU |  |  | AL |  |  |  | 6 | 225
|  |  | Max |  | Grand Total |  | AWG | 60C | 75C | 90C | 60C | 75C | 90C | AWG | 10 | 250
Note 1: | [6 empty] | 14 | 15 | 20 | 25 | -- | -- | -- | 14 | 15 | 300
No temperature correction needed. No derating for number of current carrying conductors in the conduit is needed. The equipment is inside a temperature controlled building. | [6 empty] | 12 | 20 | 25 | 30 | 15 | 20 | 25 | 12 | 20 | 350
[7 empty] | 10 | 30 | 35 | 40 | 25 | 30 | 35 | 10 | 25 | 400
[7 empty] | 8 | 40 | 50 | 55 | 35 | 40 | 45 | 8 | 30 | 450
[7 empty] | 6 | 55 | 65 | 75 | 40 | 50 | 55 | 6 | 35 | 500
[7 empty] | 4 | 70 | 85 | 95 | 55 | 65 | 75 | 4 | 40 | 600
Note 2: | [6 empty] | 3 | 85 | 100 | 115 | 65 | 75 | 85 | 3 | 45 | 700
This calculation is for a motor feeder. The largest motor is calculated at 125%,see 430.24. Since the ampacity is over 100A, see 110.14C, use the 75C column. Use #1 CU for the feeder. | [6 empty] | 2 | 95 | 115 | 130 | 75 | 90 | 100 | 2 | 50 | 800
[7 empty] | 1 | 110 | 130 | 145 | 85 | 100 | 115 | 1 | 60 | 1000
[7 empty] | 1/O | 125 | 150 | 170 | 100 | 120 | 135 | 1/O | 70 | 1200
[7 empty] | 2/O | 145 | 175 | 195 | 115 | 135 | 150 | 2/O | 80 | 1600
[7 empty] | 3/O | 165 | 200 | 225 | 130 | 155 | 175 | 3/O | 90 | 2000
Note 3: | [6 empty] | 4/O | 195 | 230 | 260 | 150 | 180 | 205 | 4/O | 100 | 2500
[7 empty] | 250 | 215 | 255 | 290 | 170 | 205 | 230 | 250 | 110 | 3000
[7 empty] | 300 | 240 | 285 | 320 | 195 | 230 | 260 | 300 | 125 | 4000
[7 empty] | 350 | 260 | 310 | 350 | 210 | 250 | 280 | 350 | 150 | 5000
[7 empty] | 400 | 280 | 335 | 380 | 225 | 270 | 305 | 400
[7 empty] | 500 | 320 | 380 | 430 | 260 | 310 | 350 | 500
Note 4: | [6 empty] | 600 | 350 | 420 | 475 | 285 | 340 | 385 | 600
[7 empty] | 700 | 385 | 460 | 520 | 315 | 375 | 425 | 700
[7 empty] | 750 | 400 | 475 | 535 | 320 | 385 | 435 | 750
[7 empty] | 800 | 410 | 490 | 555 | 330 | 395 | 445 | 800
[7 empty] | 900 | 435 | 520 | 585 | 355 | 425 | 480 | 900
[7 empty] | 1000 | 455 | 545 | 615 | 375 | 445 | 500 | 1000
[7 empty] | 1250 | 495 | 590 | 665 | 405 | 485 | 545 | 1250
[7 empty] | 1500 | 525 | 625 | 705 | 435 | 520 | 585 | 1500
[7 empty] | 1750 | 545 | 650 | 735 | 455 | 545 | 615 | 1750
[7 empty] | 2000 | 555 | 665 | 750 | 470 | 560 | 630 | 2000
None
Spreadsheet by: | [6 empty] | Spreadsheet by:
Lorn Macilravie, Master Electrician, 307-696-7926, risingedgeservices@gmail.com | [6 empty] | Lorn Macilravie, Master Electrician, 307-696-7926, risingedgeservices@gmail.com
For occasional spreadsheet updates, go to: https://sites.google.com/site/macilravie/ | [6 empty] | For occasional spreadsheet updates, go to: https://sites.google.com/site/macilravie/
The YELLOW cells are not protected. | [6 empty] | The YELLOW cells are not protected.

## Motor Data
MOTOR TROUBLESHOOTING | [5 empty] | DATE: | 2016-11-18 14:41
PROJECT: | F Belt Main Drive Running with Coal. Size 6 Across the Line Starter
NOTES: | Measurements taken by Lorn MacIlravie. Meters: Fluke 87, AEMC PowerPad, Fluke Amp Clamp
Phase to Phase Voltage | AB | 475.4 | Volts | 0.73333 | Average P-P Volts | 474.6667 | Write your notes here.
| AC | 475.4 | Volts | 0.73333 | Unbalance | 0.309%
| BC | 473.2 | Volts | 1.4667
Phase to Ground Voltage | Phase A | 273.2 | Volts | 1.4 | Average P-G Volts | 271.8 | Write your notes here.
| Phase B | 272.9 | Volts | 1.1 | Unbalance | 0.9198%
| Phase C | 269.3 | Volts | 2.5
Motor Amperage | Phase A | 201 | Amps | 0.33333 | Average Motor Amps | 201.3333 | Coal on belt.
| Phase B | 207 | Amps | 5.6667 | Unbalance | 2.815%
| Phase C | 196 | Amps | 5.3333
DC Bus Voltage, Measured |  | 0 | VDC |  | Average P - P Volts*1.414= | 671.28 | Not a drive
Inrush Current |  | 1515 | Amps |  | Inrush/NP Amps= | 5.5292 | Fluke Amp Meter set on Inrush
Resistance across the coil |  | 460000 | Ohms
Insulation Resistance, Phase to Ground, between Breaker and Contactor | Phase A | 2200000000 | Ohms | 0 | Average Resistance P-G | 2200000000 | Avoid testing insulation resistance to ground with a drive connected to the conductors. Make sure the power is OFF.
| Phase B | 2200000000 | Ohms | 0 | Unbalance | 0%
| Phase C | 2200000000 | Ohms | 0
Insulation Resistance, Phase to Ground, between Contactor, or Drive, and the Motor | Phase A | 2200000000 | Ohms | 0 | Average Resistance P-G | 2200000000 | Avoid testing insulation resistance to ground with a drive connected to the conductors. Make sure the power is OFF.
| Phase B | 2200000000 | Ohms | 0 | Unbalance | 0%
| Phase C | 2200000000 | Ohms | 0
Insulation Resistance, Phase to Ground, at the Motor Leads. | Phase A | 2200000000 | Ohms | 0 | Average Resistance P-G | 2200000000 | Make sure the branch circuit conductors are disconnected.
| Phase B | 2200000000 | Ohms | 0 | Unbalance | 0%
| Phase C | 2200000000 | Ohms | 0
Phase to Phase Ohms, on the Branch Circuit Conductors, at the Contactor or Drive | AB | 0.15 | Ohms | 0 | Average Resistance P-P | 0.15 | A low ohm meter is a good idea, especially for large motors.
| AC | 0.15 | Ohms | 0 | Unbalance | 0%
| BC | 0.15 | Ohms | 0
Phase to Phase Ohms, on Motor Leads, at the Motor | AB | 0 | Ohms | 0 | Average Resistance P-P | 0 | Not done.
| AC | 0 | Ohms | 0 | Unbalance | #DIV/0!
| BC | 0 | Ohms | 0
DC Control Voltage |  | 132.5 | VDC
Control Transformer High Side | HIGH | 472 | Volts |  | Ratio | 3.8:1
Control Transformer Low Side | LOW | 124 | Volts
Control Transformer Size |  | 1 | KVA |  | Secondary Amperes | 8.0645 | I need to verify the actual size.
Coil Inrush Amperes |  | 6.6 | AAC
Coil Seal In Amperes |  | 0.1 | AAC
Voltage Harmonics THD | Phase A | 0.7% | THD | 0% | Average | 0.7% | Measurements taken with AEMC PowerPad.
| Phase B | 0.7% | THD | 0% | Unbalance | 0%
| Phase C | 0.7% | THD | 0%
Current Harmonics THD | Phase A | 2% | THD | 0.06667% | Average | 2.067% | Measurements taken with AEMC PowerPad.
| Phase B | 2% | THD | 0.06667% | Unbalance | 6.452%
| Phase C | 2.2% | THD | 0.1333%
Power Factor | Phase A | 0.89 | PF | 0.013333 | Average | 0.87667 | Measurements taken with AEMC PowerPad.
| Phase B | 0.86 | PF | 0.016667 | Unbalance | 1.901%
| Phase C | 0.88 | PF | 0.0033333
Manufacturer | Baldor | [5 empty] | Notes: No contact chatter on startup.
Catalog No. | B431213
Specification
HP | 250
Volts | 460
Amps | 274
RPM | 1785
Frame | 449T
HZ | 60
Phase | 3
Service Factor | 1.15
Code
Class | F
EFF | 0.95
PF | 0.891
Rating | 40C, CONTINOUS
Bearings
Enclosure | TEFC XEX
Random Calculations from Motor Data |  |  |  |  | Math Reminder
KVA calculated from HP | 186.5 |  |  |  | 1e-12 | 1e-12 | pico
Low, 115%, OL Setting | 315.1 |  |  |  | 1e-09 | 1e-09 | nano
Normal, 125%, OL Setting | 342.5 |  |  |  | 1e-06 | 1e-06 | micro
Max, 140%, OL Setting | 383.6 |  |  |  | 0.001 | 0.001 | mili
Service Factor Amps | 315.1 |  |  |  | 1 | 1 | ohms
[5 empty] | 1000 | 1000 | kilo
Spreadsheet by: |  |  |  |  | 1000000 | 1000000 | mega
Lorn MacIlravie, Master Electrician |  |  |  |  | 1000000000 | 1000000000 | giga
risingedgeservices@gmail.com |  |  |  |  | 1000000000000 | 1000000000000 | tera
Mobile: 307-696-7926
The YELLOW cells are not protected.

## VFD Test
VFD TROUBLESHOOTING WITHOUT POWER | [5 empty] | DATE: | 2016-12-01 11:00
PROJECT: | SPX9000 Drive from Fan 14
NOTES: | Measurements taken by Lorn MacIlravie
TURN THE POWER OFF.
You need a meter with diode testing capability, such as a Fluke 87.
Part 1: Basic Checks
Check power on the LINE side of the drive, LINE to GROUND |  | Set meter to VAC
|  | Expected Value | Actual Value
- Black Lead to GROUND | + Red Lead to L1 | 0 | 0 |  | Notes:
- Black Lead to GROUND | + Red Lead to L2 | 0 | 0
- Black Lead to GROUND | + Red Lead to L3 | 0 | 0
Check power on the LINE side of the drive, PHASE to PHASE |  | Set meter to VAC
|  | Expected Value | Actual Value
- Black Lead to L1 | + Red Lead to L2 | 0 | 0 |  | Notes:
- Black Lead to L1 | + Red Lead to L3 | 0 | 0
- Black Lead to L2 | + Red Lead to L3 | 0 | 0
Check power on the DC Bus |  | Set meter to VDC
|  | Expected Value | Actual Value
- Black Lead to NEG. BUS TERMINAL | + Red Lead to POS. BUS TERM. | 0 | 0 |  | Notes:
- Black Lead to GROUND | + Red Lead to POS. BUS TERM. | 0 | 0
- Black Lead to GROUND | + Red Lead to NEG. BUS TERM. | 0 | 0
Check for ground faults on the LINE side of the drive. |  | Set meter to OHMS
|  | Expected Value | Actual Value
- Black Lead to GROUND | + Red Lead to L1 | > 1 Megaohm to OL | 13000000 |  | Notes:
- Black Lead to GROUND | + Red Lead to L2 | > 1 Megaohm to OL | 13000000
- Black Lead to GROUND | + Red Lead to L3 | > 1 Megaohm to OL | 13000000
Check for ground faults on the LOAD side of the drive. |  | Set meter to OHMS
|  | Expected Value | Actual Value
- Black Lead to GROUND | + Red Lead to T1 | > 1 Megaohm to OL | 10000000 |  | Notes:
- Black Lead to GROUND | + Red Lead to T2 | > 1 Megaohm to OL | 10000000
- Black Lead to GROUND | + Red Lead to T3 | > 1 Megaohm to OL | 10000000
Part 2: Component Checks on Converter
DC Converter Test 1 |  | Set meter to DIODE
|  | Expected Value | Actual Value
- Black Lead to L1 | + Red Lead to POS. BUS TERM. | OL | OL |  | Notes: Value should slowly increase to OL.
- Black Lead to L2 | + Red Lead to POS. BUS TERM. | OL | OL
- Black Lead to L3 | + Red Lead to POS. BUS TERM. | OL | OL
DC Converter Test 2 |  | Set meter to DIODE
|  | Expected Value | Actual Value
- Black Lead to L1 | + Red Lead to NEG. BUS TERM. | +/- 0.25 VDC to 1.00 VDC | 0.382 |  | Notes:
- Black Lead to L2 | + Red Lead to NEG. BUS TERM. | +/- 0.25 VDC to 1.00 VDC | 0.38
- Black Lead to L3 | + Red Lead to NEG. BUS TERM. | +/- 0.25 VDC to 1.00 VDC | 0.378
DC Converter Test 3 |  | Set meter to DIODE
|  | Expected Value | Actual Value
- Black Lead to POS. BUS TERMINAL | + Red Lead to L1 | +/- 0.25 VDC to 1.00 VDC | 1.03 |  | Notes:
- Black Lead to POS. BUS TERMINAL | + Red Lead to L2 | +/- 0.25 VDC to 1.00 VDC | 0.996
- Black Lead to POS. BUS TERMINAL | + Red Lead to L3 | +/- 0.25 VDC to 1.00 VDC | 1.007
DC Converter Test 4 |  | Set meter to DIODE
|  | Expected Value | Actual Value
- Black Lead to NEG. BUS TERMINAL | + Red Lead to L1 | OL | OL |  | Value should slowly increase to OL.
- Black Lead to NEG. BUS TERMINAL | + Red Lead to L2 | OL | OL
- Black Lead to NEG. BUS TERMINAL | + Red Lead to L3 | OL | OL
Part 3: Component Checks on Inverter
DC Inverter Test 1 |  | Set meter to DIODE
|  | Expected Value | Actual Value
- Black Lead to T1 | + Red Lead to POS. BUS TERM. | OL | OL |  | Value should slowly increase to OL.
- Black Lead to T2 | + Red Lead to POS. BUS TERM. | OL | OL
- Black Lead to T3 | + Red Lead to POS. BUS TERM. | OL | OL
DC Inverter Test 2 |  | Set meter to DIODE
|  | Expected Value | Actual Value
- Black Lead to T1 | + Red Lead to NEG. BUS TERM. | +/- 0.25 VDC to 1.00 VDC | 0.282 |  | Notes:
- Black Lead to T2 | + Red Lead to NEG. BUS TERM. | +/- 0.25 VDC to 1.00 VDC | 0.257
- Black Lead to T3 | + Red Lead to NEG. BUS TERM. | +/- 0.25 VDC to 1.00 VDC | 0.294
DC Inverter Test 3 |  | Set meter to DIODE
|  | Expected Value | Actual Value
- Black Lead to POS. BUS TERMINAL | + Red Lead to T1 | +/- 0.25 VDC to 1.00 VDC | 0.284 |  | Notes:
- Black Lead to POS. BUS TERMINAL | + Red Lead to T2 | +/- 0.25 VDC to 1.00 VDC | 0.263
- Black Lead to POS. BUS TERMINAL | + Red Lead to T3 | +/- 0.25 VDC to 1.00 VDC | 0.294
DC Inverter Test 4 |  | Set meter to DIODE
|  | Expected Value | Actual Value
- Black Lead to NEG. BUS TERMINAL | + Red Lead to T1 | OL | OL |  | Value should slowly increase to OL.
- Black Lead to NEG. BUS TERMINAL | + Red Lead to T2 | OL | OL
- Black Lead to NEG. BUS TERMINAL | + Red Lead to T3 | OL | OL
Part 4: DC Bus Checks
DC Bus Check 1 |  | Set meter to DIODE
|  | Expected Value | Actual Value
- Black Lead to NEG. BUS TERMINAL | + Red Lead to POS. BUS TERM. | OL | OL |  | This test slowly charges the capacitor up to about 3 VDC.
DC Bus Check 2 |  | Set meter to VDC
|  | Expected Value | Actual Value
- Black Lead to NEG. BUS TERMINAL | + Red Lead to POS. BUS TERM. | 3 VDC to 0 VDC | 2.9 |  | This test checks the voltage that DC Bus Check 1 left on the caps. You should expect it to be slowly dropping, eventually to zero.
DC Bus Check 3 |  | Set meter to OHMS
|  | Expected Value | Actual Value
- Black Lead to GROUND | + Red Lead to POS. BUS TERM. | >1 Mega ohm | 19000000 |  | Value should slowly increase to OL.
- Black Lead to GROUND | + Red Lead to NEG. BUS TERM.
Spreadsheet by: |  | Math Reminder
Lorn Macilravie, Master Electrician |  | 1e-12 | 1e-12 | pico
risingedgeservices@gmail.com |  | 1e-09 | 1e-09 | nano
Mobile: 307-696-7926 |  | 1e-06 | 1e-06 | micro
The YELLOW cells are not protected. |  | 0.001 | 0.001 | mili
|  | 1 | 1 | ohms
|  | 1000 | 1000 | kilo
|  | 1000000 | 1000000 | mega
|  | 1000000000 | 1000000000 | giga
|  | 1000000000000 | 1000000000000 | tera

## Rod Pump Flow
API Rod Pump Flow Calculation
Change the values in the highlighted cells.
Standard Calculation |  | Table Version
55 | Stroke Length (Inches) | 55 | Stroke Length (Inches) |  | 1.5 | Bore Diameter (Inches)
1.5 | Bore Diameter (Inches)
9 | SPM | SPM | 90% Eff. | 85% Eff. | 80% Eff. | 75% Eff. | 70% Eff. | 60%
129.8632 | BPD = (Bore Dia. X Bore Dia.) X 0.1166 X Stroke Length X SPM | 1 | 12.9863 | 12.2649 | 11.5434 | 10.8219 | 10.1005 | 8.6575
80% | Efficiency | 2 | 25.9726 | 24.5297 | 23.0868 | 21.6439 | 20.2009 | 17.3151
103.8906 | BPD x Eff. | 3 | 38.959 | 36.7946 | 34.6302 | 32.4658 | 30.3014 | 25.9726
|  | 4 | 51.9453 | 49.0594 | 46.1736 | 43.2877 | 40.4019 | 34.6302
|  | 5 | 64.9316 | 61.3243 | 57.717 | 54.1097 | 50.5024 | 43.2877
Spreadsheet by: |  | 6 | 77.9179 | 73.5892 | 69.2604 | 64.9316 | 60.6028 | 51.9453
Lorn Macilravie, Master Electrician |  | 7 | 90.9043 | 85.854 | 80.8038 | 75.7536 | 70.7033 | 60.6028
risingedgeservices@gmail.com |  | 8 | 103.8906 | 98.1189 | 92.3472 | 86.5755 | 80.8038 | 69.2604
Mobile: 307-696-7926 |  | 9 | 116.8769 | 110.3838 | 103.8906 | 97.3974 | 90.9043 | 77.9179
The YELLOW cells are not protected. |  | 10 | 129.8632 | 122.6486 | 115.434 | 108.2194 | 101.0047 | 86.5755
|  | 11 | 142.8496 | 134.9135 | 126.9774 | 119.0413 | 111.1052 | 95.233
|  | 12 | 155.8359 | 147.1783 | 138.5208 | 129.8632 | 121.2057 | 103.8906
|  | 9 | 116.8769 | 110.3838 | 103.8906 | 97.3974 | 90.9043 | 77.9179

## Diff 2 Dates
Date in the past | 2011-05-18
More recent date | 2011-09-06
Difference | 0 years, 3 months, 19 days
Date in the past | 1950-01-01
Today | 2018-02-17 18:48
Difference | 68 years, 1 months, 16.7831232638855 days
Today | 2018-02-17
Add Days | 20 | 2018-03-09
Add Weeks | 7 | 2018-04-07
Add Months | 18 | 2019-08-17
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## Resistors
4 Band Resistors |  |  |  |  | 1st Band | 2nd Band | 3rd Band | 4th Band |  |  | 2016-11-15
|  |  |  | Color |  |  | Multiplier | Tolerance
First Band | Red | First Significant Digit | 2 | Black | 0 | 0 | 1 |  |  | Math Reminder
Second Band | Green | Second Significant Digit | 5 | Brown | 1 | 1 | 10 |  |  | 1e-12 | 1e-12 | pico
Third Band | Brown | Multiplier | 10 | Red | 2 | 2 | 100 |  |  | 1e-09 | 1e-09 | nano
Fourth Band | Gold | Tolerance | 5% | Orange | 3 | 3 | 1000 |  |  | 1e-06 | 1e-06 | micro
Calculated Value | 250 | Ohms |  | Yellow | 4 | 4 | 10000 |  |  | 0.001 | 0.001 | mili
Calculated Value | 250 Ω |  |  | Green | 5 | 5 | 100000 |  |  | 1 | 1 | ohms
|  |  |  | Blue | 6 | 6 | 100000 |  |  | 1000 | 1000 | kilo
| 25 | Digits |  | Violet | 7 | 7 | 10000000 |  |  | 1000000 | 1000000 | mega
| 10 | Multiplier |  | Gray | 8 | 8 | 100000000 |  |  | 1000000000 | 1000000000 | giga
| 250 | Calculated Value | 100% | White | 9 | 9 | 1000000000 |  |  | 1000000000000 | 1000000000000 | tera
| 262.5 | Max Value | 105% | Gold |  |  | 0.1 | 5%
| 237.5 | Min Value | 95% | Silver |  |  | 0.01 | 10%
|  |  |  | None |  |  |  | 20%
5 Band Precision Resistors |  |  |  |  | 1st Band | 2nd Band | 3rd Band | 4th Band | 5th Band |  |  | 5th Band
|  |  |  | Color |  |  |  | Multiplier | Tolerance |  | Color | Tolerance
First Band | Red | First Significant Digit | 2 | Black | 0 | 0 | 0 | 1 |  |  | Brown | 1%
Second Band | Green | Second Significant Digit | 5 | Brown | 1 | 1 | 1 | 10 | 1% |  | Red | 2%
Third Band | Black | Third Significant Digit | 0 | Red | 2 | 2 | 2 | 100 | 2% |  | Green | 0.5%
Fourth Band | Black | Multiplier | 1 | Orange | 3 | 3 | 3 | 1000 |  |  | Blue | 0.25%
Fifth Band | Brown | Tolerance | 1% | Yellow | 4 | 4 | 4 | 10000 |  |  | Violet | 0.1%
Calculated Value | 250 | Ohms |  | Green | 5 | 5 | 5 | 100000 | 0.5%
Calculated Value | 250 Ω |  |  | Blue | 6 | 6 | 6 | 100000 | 0.25%
|  |  |  | Violet | 7 | 7 | 7 | 10000000 | 0.1%
| 250 | Digits |  | Gray | 8 | 8 | 8 | 100000000
| 1 | Multiplier |  | White | 9 | 9 | 9 | 1000000000
| 250 | Calculated Value | 100% | Gold |  |  |  | 0.1
| 252.5 | Max Value | 101% | Silver |  |  |  | 0.01
| 247.5 | Min Value | 99%
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## Quick Load
QUICK LOAD CALCULATOR | [7 empty] | 2016-11-02
NAME | I | V | PF | EFF | 1 OR 1.73 | KW | KVA | HP
Heater | 24.057 | 480 | 1 | 1 | 1.732 | 20 | 20 | 26.8097
142A | 1696 | 480 | 0.8 | 0.9 | 1.732 | 1127.9892 | 1409.9866 | 1360.8449
141B | 0 | 480 | 0.8 | 0.9 | 1.732 | 0 | 0 | 0
141A1 | 162 | 480 | 0.8 | 0.9 | 1.732 | 107.7443 | 134.6803 | 129.9864
| 162 | 480 | 0.8 | 0.9 | 1.732 | 107.7443 | 134.6803 | 129.9864
| 162 | 480 | 0.8 | 0.9 | 1.732 | 107.7443 | 134.6803 | 129.9864
| 162 | 480 | 0.8 | 0.9 | 1.732 | 107.7443 | 134.6803 | 129.9864
| 162 | 480 | 0.8 | 0.9 | 1.732 | 107.7443 | 134.6803 | 129.9864
| 162 | 480 | 0.8 | 0.9 | 1.732 | 107.7443 | 134.6803 | 129.9864
| 162 | 480 | 0.8 | 0.9 | 1.732 | 107.7443 | 134.6803 | 129.9864
| 162 | 480 | 0.8 | 0.9 | 1.732 | 107.7443 | 134.6803 | 129.9864
| 162 | 480 | 0.8 | 0.9 | 1.732 | 107.7443 | 134.6803 | 129.9864
| 162 | 480 | 0.8 | 0.9 | 1.732 | 107.7443 | 134.6803 | 129.9864
| 162 | 480 | 0.8 | 0.9 | 1.732 | 107.7443 | 134.6803 | 129.9864
| 162 | 480 | 0.8 | 0.9 | 1.732 | 107.7443 | 134.6803 | 129.9864
| 162 | 480 | 0.8 | 0.9 | 1.732 | 107.7443 | 134.6803 | 129.9864
| 162 | 480 | 0.8 | 0.9 | 1.732 | 107.7443 | 134.6803 | 129.9864
|  | 480 | 0.8 | 0.9 | 1.732 | 0 | 0 | 0
143B1 | 168 | 480 | 0.8 | 0.9 | 1.732 | 111.7348 | 139.6685 | 134.8007
142B | 1956 | 480 | 0.8 | 0.9 | 1.732 | 1300.9121 | 1626.1402 | 1569.465
143B | 2049 | 480 | 0.8 | 0.9 | 1.732 | 1362.7653 | 1703.4566 | 1644.0868
143A1 | 0 | 480 | 0.8 | 0.9 | 1.732 | 0 | 0 | 0
143A | 1944 | 480 | 0.8 | 0.9 | 1.732 | 1292.9311 | 1616.1638 | 1559.8364
[5 empty] | TOTALS | 6724.7521 | 8400.9402 | 8115.6527
| KVA | KW | HP | V | PF | EFF | 1 OR 1.73 | I
| 20 | 16 | 19.3029 | 480 | 0.8 | 0.9 | 1.732 | 24.057
| 150 | 120 | 144.7721 | 480 | 0.8 | 0.9 | 1.732 | 180.4273
| 150.0289 | 120.0231 | 144.8 | 480 | 0.8 | 0.9 | 1.732 | 180.462
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## Bucket Test
BUCKET TEST
60 | SECONDS TO FILL 5 GAL BUCKET
5 | GPM
171.4286 | BBLS/D
TURBINE METER
910 | K FACTOR
10000 | ACTUAL READING
10.989 | GPM
376.7661 | BBLS/D
WATER LEVEL
15 | DOWN HOLE PSIG
2 | CASING PSIG
30.0231 | FEET OF FRESH WATER (PSI/0.433)
29.5455 | FEET OF PRODUCED WATER (PSI/0.44)
DIFFERENTIAL TRANSDUCERS
100 | TOP HOLE TRANSDUCER RANGE
300 | BOTTOM HOLE TRANSDUCER RANGE
6 | TOP HOLE TRANSDUCER mA
20 | BOTTOM HOLE TRANSDUCER mA READING
12.5 | TOP HOLE PSIG
300 | BOTTOM HOLE PSIG
663.9723 | FEET OF FRESH WATER (PSI/0.433)
653.4091 | FEET OF PRODUCED WATER (PSI/0.44)
SIGNAL SCALING
100 | HIGH SCALE
0 | LOW SCALE
20 | HIGH SIGNAL
4 | LOW SIGNAL
12 | CURRENT SIGNAL VALUE
50 | CURRENT SCALED VALUE
TANK VOLUME CALCULATIONS
20 | HIGHT OF TANK (FT.) | INCHES | DECIMAL
12 | DIAMETER OF TANK (FT.) | 12 | 1
2261.952 | TOTAL VOLUME IN CUBIC FEET | 11 | 0.91667
16920.576 | TOTAL VOLUME IN GALLONS | 10 | 0.83333
402.8709 | TOTAL VOLUME IN BBLS | 9 | 0.75
5 | FEET OF WATER IN THE TANK | 8 | 0.66667
4230.144 | GALLONS IN THE TANK | 7 | 0.58333
100.7177 | BBLS IN THE TANK | 6 | 0.5
|  | 5 | 0.41667
TANK RATE CALCULATION |  | 4 | 0.33333
|  | 3 | 0.25
15 | DIAMETER OF TANK (FT.) | 2 | 0.16667
5 | FIRST GAUGE (FT.) | 1 | 0.083333
10 | SECOND GAUGE (FT.)
30 | MINUTES BETWEEN GAUGE TIMES
31.4743 | TANK VOLUME (BBLS PER FOOT)
157.3714 | VOLUME AT FIRST GAUGING
314.7429 | VOLUME AT SECOND GAUGING
5.2457 | BBLS/MINUTE
220.32 | GALLONS/MINUTE
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## NEMA SIZE
Maximum Horsepower - Polyphase Motors
NEMA | Full Voltage Starting |  |  | Auto Transformer Starting
Size | 200V | 230V | 460V 575V | 200V | 230V | 460V 575V
0 | 1 ½ | 1 ½ | 2 | -- | -- | --
0 | 3 | 3 | 5 | -- | -- | --
1 | 7 ½ | 7 ½ | 10 | 7 ½ | 7 ½ | 10
2 | 10 | 15 | 25 | 10 | 15 | 25
3 | 25 | 30 | 50 | 25 | 30 | 50
4 | 40 | 50 | 100 | 40 | 50 | 100
5 | 75 | 100 | 200 | 75 | 100 | 200
6 | 150 | 200 | 400 | 150 | 200 | 400
7 | -- | 300 | 600 | -- | 300 | 600
8 | -- | 450 | 900 | -- | 450 | 900
9 | -- | 800 | 1600 | -- | 800 | 1600
NEMA | Part Winding Starting |  |  | Wye Delta Starting
Size | 200V | 230V | 460V 575V | 200V | 230V | 460V 575V
0 | -- | -- | -- | -- | -- | --
0 | -- | -- | -- | -- | -- | --
1 | 10 | 10 | 15 | 10 | 10 | 15
2 | 20 | 25 | 40 | 20 | 25 | 40
3 | 40 | 50 | 75 | 40 | 50 | 75
4 | 75 | 75 | 150 | 60 | 75 | 150
5 | 150 | 150 | 350 | 150 | 150 | 300
6 | -- | 300 | 600 | 300 | 350 | 700
7 | -- | 450 | 900 | 500 | 500 | 1000
8 | -- | 700 | 1400 | 750 | 800 | 1500
9 | -- | 1300 | 2600 | 1500 | 1500 | 3000
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## Transducers
TRANSDUCERS
PSI RANGE | MAX DEPTH
15 | 34.65
100 | 231
250 | 577.5
350 | 808.5
500 | 1155
1000 | 2310
12 | mA
250 | RANGE
125 | PSI
288.75 | FEET
15.625 | PSI/mA
PSI BOTTOM | 100
PSI TOP | 50 | -
| 50 | X 2.31 = | 115.5 | FEET OF WATER
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## GAIN BIAS
IN MIN | 0
IN MAX | 20
OUT MIN | 0
OUT MAX | 10
CALCULATED GAIN |  | 0.5
CALCULATED BIAS |  | 0
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## MARKUP
168 | 168 | 168 | 168 | Cost
25 | 20 | 20 | 25.3333 | Points
133.3% | 125% | 125% | 133.9% | Markup
0.75 | 0.8 | 0.8 | 0.74667 | Margin
224 | 210 | 210 | 225 | Sales/List Price
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## BHP
BRAKE HORSE POWER
COMMON GPM FORMULA
100 | GPM
30 | INLET PSI
2500 | OUTLET PSI
5705.7 | FT. THD
1 | SG
3960 | CONSTANT
0.9 | PUMP EFF.
160.0926 | BHP | GPM X TDH X SG / 3960 X PUMP EFF.
COMMON BPD FORMULA
3428.6 | BPD
0 | INLET PSI
2500 | OUTLET PSI
5775 | FT. THD
1 | SG
1.7 | CONSTANT
0.9 | PUMP EFF.
161.9061 | BHP | 1.7 X BPD X PSI X SG / 100,000 X PUMP EFF.
WEATHERFORD FORMULA
3428.6 | BPD
2500 | PSI
58800 | CONSTANT
0.9 | PUMP EFF.
161.9709 | BHP | BPD X PSI / 58800 X PUMP EFF.
Misc. Conversions
100 | GPM
3428.5714 | BPD
3428.6 | BPD
100.0008 | GPM
0 | INLET PSI
2500 | OUTLET PSI
5775 | FT. THD
5775 | FT. THD
2500 | PSI
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## RPM
MOTOR SHAFT RPM
Name Plate Volts |  | 480
Name Plate HZ |  | 60
V/HZ |  | 8
SLIP |  | 4%
|  | 3600 | 1800 | 1200 | 900 | 720 | 600 | 514.2857 | 450 | 400 | RPM
VOLTS | HZ | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | POLES
480 | 60 | 3456 | 1728 | 1152 | 864 | 691.2 | 576 | 493.7143 | 432 | 384
480 | 60 | 3456 | 1728 | 1152 | 864 | 691.2 | 576 | 493.7143 | 432 | 384
472 | 59 | 3398.4 | 1699.2 | 1132.8 | 849.6 | 679.68 | 566.4 | 485.4857 | 424.8 | 377.6
464 | 58 | 3340.8 | 1670.4 | 1113.6 | 835.2 | 668.16 | 556.8 | 477.2571 | 417.6 | 371.2
456 | 57 | 3283.2 | 1641.6 | 1094.4 | 820.8 | 656.64 | 547.2 | 469.0286 | 410.4 | 364.8
448 | 56 | 3225.6 | 1612.8 | 1075.2 | 806.4 | 645.12 | 537.6 | 460.8 | 403.2 | 358.4
440 | 55 | 3168 | 1584 | 1056 | 792 | 633.6 | 528 | 452.5714 | 396 | 352
432 | 54 | 3110.4 | 1555.2 | 1036.8 | 777.6 | 622.08 | 518.4 | 444.3429 | 388.8 | 345.6
424 | 53 | 3052.8 | 1526.4 | 1017.6 | 763.2 | 610.56 | 508.8 | 436.1143 | 381.6 | 339.2
416 | 52 | 2995.2 | 1497.6 | 998.4 | 748.8 | 599.04 | 499.2 | 427.8857 | 374.4 | 332.8
408 | 51 | 2937.6 | 1468.8 | 979.2 | 734.4 | 587.52 | 489.6 | 419.6571 | 367.2 | 326.4
400 | 50 | 2880 | 1440 | 960 | 720 | 576 | 480 | 411.4286 | 360 | 320
392 | 49 | 2822.4 | 1411.2 | 940.8 | 705.6 | 564.48 | 470.4 | 403.2 | 352.8 | 313.6
384 | 48 | 2764.8 | 1382.4 | 921.6 | 691.2 | 552.96 | 460.8 | 394.9714 | 345.6 | 307.2
376 | 47 | 2707.2 | 1353.6 | 902.4 | 676.8 | 541.44 | 451.2 | 386.7429 | 338.4 | 300.8
368 | 46 | 2649.6 | 1324.8 | 883.2 | 662.4 | 529.92 | 441.6 | 378.5143 | 331.2 | 294.4
360 | 45 | 2592 | 1296 | 864 | 648 | 518.4 | 432 | 370.2857 | 324 | 288
352 | 44 | 2534.4 | 1267.2 | 844.8 | 633.6 | 506.88 | 422.4 | 362.0571 | 316.8 | 281.6
344 | 43 | 2476.8 | 1238.4 | 825.6 | 619.2 | 495.36 | 412.8 | 353.8286 | 309.6 | 275.2
336 | 42 | 2419.2 | 1209.6 | 806.4 | 604.8 | 483.84 | 403.2 | 345.6 | 302.4 | 268.8
328 | 41 | 2361.6 | 1180.8 | 787.2 | 590.4 | 472.32 | 393.6 | 337.3714 | 295.2 | 262.4
320 | 40 | 2304 | 1152 | 768 | 576 | 460.8 | 384 | 329.1429 | 288 | 256
312 | 39 | 2246.4 | 1123.2 | 748.8 | 561.6 | 449.28 | 374.4 | 320.9143 | 280.8 | 249.6
304 | 38 | 2188.8 | 1094.4 | 729.6 | 547.2 | 437.76 | 364.8 | 312.6857 | 273.6 | 243.2
296 | 37 | 2131.2 | 1065.6 | 710.4 | 532.8 | 426.24 | 355.2 | 304.4571 | 266.4 | 236.8
288 | 36 | 2073.6 | 1036.8 | 691.2 | 518.4 | 414.72 | 345.6 | 296.2286 | 259.2 | 230.4
280 | 35 | 2016 | 1008 | 672 | 504 | 403.2 | 336 | 288 | 252 | 224
272 | 34 | 1958.4 | 979.2 | 652.8 | 489.6 | 391.68 | 326.4 | 279.7714 | 244.8 | 217.6
264 | 33 | 1900.8 | 950.4 | 633.6 | 475.2 | 380.16 | 316.8 | 271.5429 | 237.6 | 211.2
256 | 32 | 1843.2 | 921.6 | 614.4 | 460.8 | 368.64 | 307.2 | 263.3143 | 230.4 | 204.8
248 | 31 | 1785.6 | 892.8 | 595.2 | 446.4 | 357.12 | 297.6 | 255.0857 | 223.2 | 198.4
240 | 30 | 1728 | 864 | 576 | 432 | 345.6 | 288 | 246.8571 | 216 | 192
232 | 29 | 1670.4 | 835.2 | 556.8 | 417.6 | 334.08 | 278.4 | 238.6286 | 208.8 | 185.6
224 | 28 | 1612.8 | 806.4 | 537.6 | 403.2 | 322.56 | 268.8 | 230.4 | 201.6 | 179.2
216 | 27 | 1555.2 | 777.6 | 518.4 | 388.8 | 311.04 | 259.2 | 222.1714 | 194.4 | 172.8
208 | 26 | 1497.6 | 748.8 | 499.2 | 374.4 | 299.52 | 249.6 | 213.9429 | 187.2 | 166.4
200 | 25 | 1440 | 720 | 480 | 360 | 288 | 240 | 205.7143 | 180 | 160
Table Calculation: Shaft RPM=(RPM*(Name Plate HZ/60))-((RPM*(Name Plate (HZ/60))*SLIP)
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## Torque
MOTOR TORQUE
4% | SLIP
60 | HZ, 50 or 60
|  | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | POLES
|  | 3600 | 1800 | 1200 | 900 | 720 | 600 | 514.2857 | 450 | 400 | BASE RPM | =(120*HZ)/Poles
KW | HP | 3456 | 1728 | 1152 | 864 | 691.2 | 576 | 493.7143 | 432 | 384 | MOTOR RPM | =BASE RPM-(BASE RPM*SLIP)
0.373 | 0.5 | 0.75984 | 1.5197 | 2.2795 | 3.0394 | 3.7992 | 4.559 | 5.3189 | 6.0787 | 6.8385
0.5595 | 0.75 | 1.1398 | 2.2795 | 3.4193 | 4.559 | 5.6988 | 6.8385 | 7.9783 | 9.1181 | 10.2578
0.746 | 1 | 1.5197 | 3.0394 | 4.559 | 6.0787 | 7.5984 | 9.1181 | 10.6377 | 12.1574 | 13.6771
1.119 | 1.5 | 2.2795 | 4.559 | 6.8385 | 9.1181 | 11.3976 | 13.6771 | 15.9566 | 18.2361 | 20.5156
1.492 | 2 | 3.0394 | 6.0787 | 9.1181 | 12.1574 | 15.1968 | 18.2361 | 21.2755 | 24.3148 | 27.3542
2.238 | 3 | 4.559 | 9.1181 | 13.6771 | 18.2361 | 22.7951 | 27.3542 | 31.9132 | 36.4722 | 41.0312
3.73 | 5 | 7.5984 | 15.1968 | 22.7951 | 30.3935 | 37.9919 | 45.5903 | 53.1887 | 60.787 | 68.3854
5.595 | 7.5 | 11.3976 | 22.7951 | 34.1927 | 45.5903 | 56.9878 | 68.3854 | 79.783 | 91.1806 | 102.5781
7.46 | 10 | 15.1968 | 30.3935 | 45.5903 | 60.787 | 75.9838 | 91.1806 | 106.3773 | 121.5741 | 136.7708
11.19 | 15 | 22.7951 | 45.5903 | 68.3854 | 91.1806 | 113.9757 | 136.7708 | 159.566 | 182.3611 | 205.1562
14.92 | 20 | 30.3935 | 60.787 | 91.1806 | 121.5741 | 151.9676 | 182.3611 | 212.7546 | 243.1481 | 273.5417
18.65 | 25 | 37.9919 | 75.9838 | 113.9757 | 151.9676 | 189.9595 | 227.9514 | 265.9433 | 303.9352 | 341.9271
22.38 | 30 | 45.5903 | 91.1806 | 136.7708 | 182.3611 | 227.9514 | 273.5417 | 319.1319 | 364.7222 | 410.3125
29.84 | 40 | 60.787 | 121.5741 | 182.3611 | 243.1481 | 303.9352 | 364.7222 | 425.5093 | 486.2963 | 547.0833
37.3 | 50 | 75.9838 | 151.9676 | 227.9514 | 303.9352 | 379.919 | 455.9028 | 531.8866 | 607.8704 | 683.8542
44.76 | 60 | 91.1806 | 182.3611 | 273.5417 | 364.7222 | 455.9028 | 547.0833 | 638.2639 | 729.4444 | 820.625
55.95 | 75 | 113.9757 | 227.9514 | 341.9271 | 455.9028 | 569.8785 | 683.8542 | 797.8299 | 911.8056 | 1025.7812
74.6 | 100 | 151.9676 | 303.9352 | 455.9028 | 607.8704 | 759.838 | 911.8056 | 1063.7731 | 1215.7407 | 1367.7083
93.25 | 125 | 189.9595 | 379.919 | 569.8785 | 759.838 | 949.7975 | 1139.7569 | 1329.7164 | 1519.6759 | 1709.6354
111.9 | 150 | 227.9514 | 455.9028 | 683.8542 | 911.8056 | 1139.7569 | 1367.7083 | 1595.6597 | 1823.6111 | 2051.5625
149.2 | 200 | 303.9352 | 607.8704 | 911.8056 | 1215.7407 | 1519.6759 | 1823.6111 | 2127.5463 | 2431.4815 | 2735.4167
186.5 | 250 | 379.919 | 759.838 | 1139.7569 | 1519.6759 | 1899.5949 | 2279.5139 | 2659.4329 | 3039.3519 | 3419.2708
223.8 | 300 | 455.9028 | 911.8056 | 1367.7083 | 1823.6111 | 2279.5139 | 2735.4167 | 3191.3194 | 3647.2222 | 4103.125
261.1 | 350 | 531.8866 | 1063.7731 | 1595.6597 | 2127.5463 | 2659.4329 | 3191.3194 | 3723.206 | 4255.0926 | 4786.9792
298.4 | 400 | 607.8704 | 1215.7407 | 1823.6111 | 2431.4815 | 3039.3519 | 3647.2222 | 4255.0926 | 4862.963 | 5470.8333
335.7 | 450 | 683.8542 | 1367.7083 | 2051.5625 | 2735.4167 | 3419.2708 | 4103.125 | 4786.9792 | 5470.8333 | 6154.6875
Table Calculation: TORQUE=(HP*5252)/MOTOR RPM
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## NEMA Temp
MOTOR WINDING TEMPERATURE EVALUATION
Chart Values in Celsius |  |  |  | Chart for the Metric Impaired
STANDARD MOTORS, 1/2 to 500HP |  | Max. Temp Rise at 40C Ambient |  | STANDARD MOTORS, 1/2 to 500HP |  | Max. Temp Rise at 104F Ambient
Ins. | Max. Temp Allowed | SF 1.15 | SF 1.0 | Ins. | Max. Temp Allowed | SF 1.15 | SF 1.0
Class | C | C | C | Class | F | F | F
A | 105 | 70 | 60 | A | 221 | 189.5 | 140
B | 130 | 90 | 80 | B | 266 | 234.5 | 176
F | 155 | 115 | 105 | F | 311 | 290.75 | 221
H | 180 | - | 125 | H | 356 | - | 257
LARGER MOTORS |  | Max. Temp Rise at 40C Ambient |  | LARGER MOTORS |  | Max. Temp Rise at 104F Ambient
Ins. | Max. Temp Allowed | SF 1.15 | SF 1.0 | Ins. | Max. Temp Allowed | SF 1.15 | SF 1.0
Class | C | C | C | Class | F | F | F
A | 105 | 70 | 60 | A | 221 | 189.5 | 140
B | 130 | 90 | 80 | B | 266 | 234.5 | 176
F | 155 | 115 | 105 | F | 311 | 290.75 | 221
H | 180 | 135 | 125 | H | 356 | 335.75 | 257
Motor Temperature Rise Calculator
B | What is the Insulation Class of the windings on your motor? |  |  |  | C | F
120 | Actual Winding Temperature, measured in degrees Celsius. |  |  |  | -40 | -40
80 | Actual Ambient Temperature, measured in degrees Celsius. |  |  |  | -30 | -22
90 | "Max. Temp Rise at 40C Ambient", from on charts above. |  |  |  | -20 | -4
130 | "Max. Temp Allowed", from charts above |  |  |  | -10 | 14
40 | Actual Temperature Rise Over Ambient |  |  |  | 0 | 32
[5 empty] | 10 | 50
[5 empty] | 20 | 68
Warning: NEMA ratings are based on an ambient temperature of 40C! |  |  |  |  | 30 | 86
[5 empty] | 40 | 104
[5 empty] | 50 | 122
[5 empty] | 60 | 140
Celsius to Fahrenheit |  |  |  |  | 70 | 158
150 | 302 |  |  |  | 80 | 176
[5 empty] | 90 | 194
Fahrenheit to Celsius |  |  |  |  | 100 | 212
98.6 | 37 |  |  |  | 110 | 230
[5 empty] | 120 | 248
Notes: |  |  |  |  | 130 | 266
Max Temp Allowed: This allows for hot spots in the motor windings |  |  |  |  | 140 | 284
NEMA rates motors at an ambient temperature of 40C. |  |  |  |  | 150 | 302
Example: 40C + (Temp Rise for a Class B, 1.15 SF Motor) = 130C, or 40C + 90C = 130C |  |  |  |  | 160 | 320
Every 10C rise in operating temperature halves the life of the windings. |  |  |  |  | 170 | 338
[5 empty] | 180 | 356
Spreadsheet by: |  |  |  |  | 190 | 374
Lorn Macilravie, Master Electrician |  |  |  |  | 200 | 392
risingedgeservices@gmail.com |  |  |  |  | 210 | 410
307-696-7926 |  |  |  |  | 220 | 428
The YELLOW cells are not protected.

## Field VD 2
POWER DROP TO WELL HEAD (W.H.) CALCULATION
|  | SOURCE TO W.H. LENGTH |  |  |  | SOURCE VOLTS |  |  | CALC. CMILS | Choose Wire (CMILS, AWG) | ACTUAL CMILS | VOLTS AT W.H. | %VD Source to W.H.
TO | SOURCE |  | 1.732 or 2 | K | AMPS |  | MAX %VD | VD | [5 empty] | Note
WELL 1 | PD1 | 4000 | 1.732 | 21.2 | 45 | 470 | 3% | 14.1 | 468745.5319 | 500000, 2 X 250 | 500000 | 456.7814 | 2.812%
WELL 2 | PD1 | 2000 | 1.732 | 21.2 | 25 | 470 | 3% | 14.1 | 130207.0922 | 133100, 2/O AWG | 133100 | 456.2065 | 2.935%
WELL 3 | PD1 | 2500 | 1.732 | 21.2 | 50 | 470 | 3% | 14.1 | 325517.7305 | 350000, 350 KCIML | 350000 | 456.8863 | 2.79%
WELL 4 | PD2 | 1000 | 1.732 | 21.2 | 25 | 470 | 3% | 14.1 | 65103.5461 | 66360, 2 AWG | 66360 | 456.167 | 2.943%
WELL 5 | PD3 | 500 | 1.732 | 21.2 | 25 | 470 | 3% | 14.1 | 32551.773 | 41740, 4 AWG | 41740 | 459.0038 | 2.34%
SURFACE TO PUMP CALCULATION
|  | DOWN HOLE LENGTH |  |  |  | VOLTS AT W.H. |  |  | CALC. CMILS | Choose Wire (CMILS, AWG) | ACTUAL CMILS | VOLTS AT PUMP | %VD Source to Pump
TO | SOURCE |  | 1.732 or 2 | K | AMPS |  | MAX %VD | VD | [5 empty] | Note
WELL 1 | PD1 | 1000 | 1.732 | 12.9 | 45 | 456.7814 | 3% | 13.7034 | 73370.3294 | 83690, 1 AWG | 83690 | 444.7677 | 5.369%
WELL 2 | PD1 | 1000 | 1.732 | 12.9 | 25 | 456.2065 | 3% | 13.6862 | 40812.6618 | 41740, 4 AWG | 41740 | 442.8243 | 5.782%
WELL 3 | PD1 | 1000 | 1.732 | 12.9 | 50 | 456.8863 | 3% | 13.7066 | 81503.869 | 83690, 1 AWG | 83690 | 443.5377 | 5.63%
WELL 4 | PD2 | 1000 | 1.732 | 12.9 | 25 | 456.167 | 3% | 13.685 | 40816.1952 | 41740, 4 AWG | 41740 | 442.7848 | 5.79%
WELL 5 | PD3 | 1000 | 1.732 | 12.9 | 25 | 459.0038 | 3% | 13.7701 | 40563.9314 | 41740, 4 AWG | 41740 | 445.6217 | 5.187%
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.
| 3 Phase, 460 | 1 Phase, 230
HP |  |  |  |  | CMILS | X2 | X3
2 | 3.4 | 12 |  | 1/O AWG | 105600 | 211200 | 316800
3 | 4.8 | 17 |  | 4/O AWG | 211600 | 423200 | 634800
5 | 7.6 | 28 |  | 250 KCIML | 250000 | 500000 | 750000
7.5 | 11 | 40
10 | 14 | 50 |  | 90% | 95% | VOLTS | 105% | 110%
15 | 21 |  |  | 99 | 104.5 | 110 | 115.5 | 121
20 | 27 |  |  | 108 | 114 | 120 | 126 | 132
25 | 34 |  |  | 207 | 218.5 | 230 | 241.5 | 253
30 | 40 |  |  | 216 | 228 | 240 | 252 | 264
40 | 52 |  |  | 414 | 437 | 460 | 483 | 506
50 | 65 |  |  | 432 | 456 | 480 | 504 | 528
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.
1.732
2
12.9
21.2
Cmils
1620, 18 AWG | 1620
2580, 16 AWG | 2580
4110, 14 AWG | 4110
6530, 12 AWG | 6530
10380, 10 AWG | 10380
16510, 8 AWG | 16510
26240, 6 AWG | 26240
41740, 4 AWG | 41740
52620, 3 AWG | 52620
66360, 2 AWG | 66360
83690, 1 AWG | 83690
105600, 1/O AWG | 105600
133100, 2/O AWG | 133100
167800, 3/O AWG | 167800
211200, 2 X 1/O | 211200
211600, 4/O AWG | 211600
250000, 250 KCIML | 250000
300000, 300 KCIML | 300000
316800, 3 X 1/O | 316800
350000, 350 KCIML | 350000
400000, 400 KCIML | 400000
423200, 2 X 4/O | 423200
500000, 2 X 250 | 500000
500000, 500 KCIML | 500000
600000, 600 KCIML | 600000
634800, 2 X 4/O | 634800
700000, 700 KCIML | 700000
750000, 3 X 250 | 750000
750000, 750 KCIML | 750000
800000, 800 KCIML | 800000
900000, 900 KCIML | 900000
1000000, 1000 KCIML | 1000000
1250000, 1250 KCIML | 1250000
1500000, 1500 KCIML | 1500000
1750000, 1750 KCIML | 1750000
2000000, 2000 KCIML | 2000000

## CM to AWG
18 | 1620 | 2 X 4/O | 423200 | 4 X 250 | 1000000 | 2 X 1000 | 2000000 | 2 X 2000 | 4000000
16 | 2580 | 500 | 500000 | 6 X 3/O | 1006800 | 4 X 500 | 2000000 | 4 X 1000 | 4000000
14 | 4110 | 2 X 250 | 500000 | 3 X 350 | 1050000 | 5 X 400 | 2000000 | 5 X 800 | 4000000
12 | 6530 | 3 X 3/O | 503400 | 5 X 4/O | 1058000 | 3 X 700 | 2100000 | 6 X 700 | 4200000
10 | 10380 | 5 X 1/O | 528000 | 2 X 600 | 1200000 | 6 X 350 | 2100000 | 3 X 1500 | 4500000
8 | 16510 | 4 X 2/O | 532400 | 3 X 400 | 1200000 | 3 X 750 | 2250000 | 5 X 900 | 4500000
6 | 26240 | 600 | 600000 | 4 X 300 | 1200000 | 3 X 800 | 2400000 | 6 X 750 | 4500000
4 | 41740 | 2 X 300 | 600000 | 1250 | 1250000 | 4 X 600 | 2400000 | 6 X 800 | 4800000
3 | 52620 | 6 X 1/O | 633600 | 5 X 250 | 1250000 | 6 X 400 | 2400000 | 4 X 1250 | 5000000
2 | 66360 | 3 X 4/O | 634800 | 6 X 4/O | 1269600 | 2 X 1250 | 2500000 | 5 X 1000 | 5000000
1 | 83690 | 5 X 2/O | 665500 | 2 X 700 | 1400000 | 5 X 500 | 2500000 | 3 X 1750 | 5250000
1/O | 105600 | 4 X 3/O | 671200 | 4 X 350 | 1400000 | 3 X 900 | 2700000 | 6 X 900 | 5400000
2/O | 133100 | 700 | 700000 | 1500 | 1500000 | 4 X 700 | 2800000 | 3 X 2000 | 6000000
3/O | 167800 | 2 X 350 | 700000 | 2 X 750 | 1500000 | 2 X 1500 | 3000000 | 4 X 1500 | 6000000
2 X 1/O | 211200 | 750 | 750000 | 3 X 500 | 1500000 | 3 X 1000 | 3000000 | 6 X 1000 | 6000000
4/O | 211600 | 3 X 250 | 750000 | 5 X 300 | 1500000 | 4 X 750 | 3000000 | 5 X 1250 | 6250000
250 | 250000 | 6 X 2/O | 798600 | 6 X 250 | 1500000 | 5 X 600 | 3000000 | 4 X 1750 | 7000000
2 X 2/O | 266200 | 800 | 800000 | 2 X 800 | 1600000 | 6 X 500 | 3000000 | 5 X 1500 | 7500000
300 | 300000 | 2 X 400 | 800000 | 4 X 400 | 1600000 | 4 X 800 | 3200000 | 6 X 1250 | 7500000
3 X 1/O | 316800 | 5 X 3/O | 839000 | 1750 | 1750000 | 2 X 1750 | 3500000 | 4 X 2000 | 8000000
2 X 3/O | 335600 | 4 X 4/O | 846400 | 5 X 350 | 1750000 | 5 X 700 | 3500000 | 5 X 1750 | 8750000
350 | 350000 | 900 | 900000 | 2 X 900 | 1800000 | 4 X 900 | 3600000 | 6 X 1500 | 9000000
3 X 2/O | 399300 | 3 X 300 | 900000 | 3 X 600 | 1800000 | 6 X 600 | 3600000 | 5 X 2000 | 10000000
400 | 400000 | 1000 | 1000000 | 6 X 300 | 1800000 | 3 X 1250 | 3750000 | 6 X 1750 | 10500000
4 X 1/O | 422400 | 2 X 500 | 1000000 | 2000 | 2000000 | 5 X 750 | 3750000 | 6 X 2000 | 12000000

## AWG to CM
WIRE SIZES - PARALLEL RUNS - AMPACITY
|  | 1X | 1X | 1X | 1X | 1X | 1X
AWG | CMILS | 60C | 75C | 90C | 60C | 75C | 90C
14 | 4110 | 15 | 20 | 25 | -- | -- | -- | 2 X 14 | 8220 | [6 empty] | 3 X 14 | 12330 | [6 empty] | 4 X 14 | 16440 | 5 X 14 | 20550 | 6 X 14 | 24660
12 | 6530 | 20 | 25 | 30 | 15 | 20 | 25 | 2 X 12 | 13060 | [6 empty] | 3 X 12 | 19590 | [6 empty] | 4 X 12 | 26120 | 5 X 12 | 32650 | 6 X 12 | 39180
10 | 10380 | 30 | 35 | 40 | 25 | 30 | 35 | 2 X 10 | 20760 | [6 empty] | 3 X 10 | 31140 | [6 empty] | 4 X 10 | 41520 | 5 X 10 | 51900 | 6 X 10 | 62280
8 | 16510 | 40 | 50 | 55 | 35 | 40 | 45 | 2 X 8 | 33020 | [6 empty] | 3 X 8 | 49530 | [6 empty] | 4 X 8 | 66040 | 5 X 8 | 82550 | 6 X 8 | 99060
6 | 26240 | 55 | 65 | 75 | 40 | 50 | 55 | 2 X 6 | 52480 | [6 empty] | 3 X 6 | 78720 | [6 empty] | 4 X 6 | 104960 | 5 X 6 | 131200 | 6 X 6 | 157440
4 | 41740 | 70 | 85 | 95 | 55 | 65 | 75 | 2 X 4 | 83480 | [6 empty] | 3 X 4 | 125220 | [6 empty] | 4 X 4 | 166960 | 5 X 4 | 208700 | 6 X 4 | 250440
3 | 52620 | 85 | 100 | 115 | 65 | 75 | 85 | 2 X 3 | 105240 | [6 empty] | 3 X 3 | 157860 | [6 empty] | 4 X 3 | 210480 | 5 X 3 | 263100 | 6 X 3 | 315720
2 | 66360 | 95 | 115 | 130 | 75 | 90 | 100 | 2 X 2 | 132720 | 2X | 2X | 2X | 2X | 2X | 2X | 3 X 2 | 199080 | 3X | 3X | 3X | 3X | 3X | 3X
1 | 83690 | 110 | 130 | 145 | 85 | 100 | 115 | AWG | CMILS | 60C | 75C | 90C | 60C | 75C | 90C | AWG | CMILS | 60C | 75C | 90C | 60C | 75C | 90C
1/O | 105600 | 125 | 150 | 170 | 100 | 120 | 135 | 2 X 1/O | 211200 | 250 | 300 | 340 | 200 | 240 | 270 | 3 X 1/O | 316800 | 375 | 450 | 510 | 300 | 360 | 405
2/O | 133100 | 145 | 175 | 195 | 115 | 135 | 150 | 2 X 2/O | 266200 | 290 | 350 | 390 | 230 | 270 | 300 | 3 X 2/O | 399300 | 435 | 525 | 585 | 345 | 405 | 450
3/O | 167800 | 165 | 200 | 225 | 130 | 155 | 175 | 2 X 3/O | 335600 | 330 | 400 | 450 | 260 | 310 | 350 | 3 X 3/O | 503400 | 495 | 600 | 675 | 390 | 465 | 525
4/O | 211600 | 195 | 230 | 260 | 150 | 180 | 205 | 2 X 4/O | 423200 | 390 | 460 | 520 | 300 | 360 | 410 | 3 X 4/O | 634800 | 585 | 690 | 780 | 450 | 540 | 615
250 | 250000 | 215 | 255 | 290 | 170 | 205 | 230 | 2 X 250 | 500000 | 430 | 510 | 580 | 340 | 410 | 460 | 3 X 250 | 750000 | 645 | 765 | 870 | 510 | 615 | 690
300 | 300000 | 240 | 285 | 320 | 195 | 230 | 260 | 2 X 300 | 600000 | 480 | 570 | 640 | 390 | 460 | 520 | 3 X 300 | 900000 | 720 | 855 | 960 | 585 | 690 | 780
350 | 350000 | 260 | 310 | 350 | 210 | 250 | 280 | 2 X 350 | 700000 | 520 | 620 | 700 | 420 | 500 | 560 | 3 X 350 | 1050000 | 780 | 930 | 1050 | 630 | 750 | 840
400 | 400000 | 280 | 335 | 380 | 225 | 270 | 305 | 2 X 400 | 800000 | 560 | 670 | 760 | 450 | 540 | 610 | 3 X 400 | 1200000 | 840 | 1005 | 1140 | 675 | 810 | 915
500 | 500000 | 320 | 380 | 430 | 260 | 310 | 350 | 2 X 500 | 1000000 | 640 | 760 | 860 | 520 | 620 | 700 | 3 X 500 | 1500000 | 960 | 1140 | 1290 | 780 | 930 | 1050
600 | 600000 | 350 | 420 | 475 | 285 | 340 | 385 | 2 X 600 | 1200000 | 700 | 840 | 950 | 570 | 680 | 770 | 3 X 600 | 1800000 | 1050 | 1260 | 1425 | 855 | 1020 | 1155
700 | 700000 | 385 | 460 | 520 | 315 | 375 | 425 | 2 X 700 | 1400000 | 770 | 920 | 1040 | 630 | 750 | 850 | 3 X 700 | 2100000 | 1155 | 1380 | 1560 | 945 | 1125 | 1275
750 | 750000 | 400 | 475 | 535 | 320 | 385 | 435 | 2 X 750 | 1500000 | 800 | 950 | 1070 | 640 | 770 | 870 | 3 X 750 | 2250000 | 1200 | 1425 | 1605 | 960 | 1155 | 1305
800 | 800000 | 410 | 490 | 555 | 330 | 395 | 445 | 2 X 800 | 1600000 | 820 | 980 | 1110 | 660 | 790 | 890 | 3 X 800 | 2400000 | 1230 | 1470 | 1665 | 990 | 1185 | 1335
900 | 900000 | 435 | 520 | 585 | 355 | 425 | 480 | 2 X 900 | 1800000 | 870 | 1040 | 1170 | 710 | 850 | 960 | 3 X 900 | 2700000 | 1305 | 1560 | 1755 | 1065 | 1275 | 1440
1000 | 1000000 | 455 | 545 | 615 | 375 | 445 | 500 | 2 X 1000 | 2000000 | 910 | 1090 | 1230 | 750 | 890 | 1000 | 3 X 1000 | 3000000 | 1365 | 1635 | 1845 | 1125 | 1335 | 1500
1250 | 1250000 | 495 | 590 | 665 | 405 | 485 | 545 | 2 X 1250 | 2500000 | 990 | 1180 | 1330 | 810 | 970 | 1090 | 3 X 1250 | 3750000 | 1485 | 1770 | 1995 | 1215 | 1455 | 1635
1500 | 1500000 | 525 | 625 | 705 | 435 | 520 | 585 | 2 X 1500 | 3000000 | 1050 | 1250 | 1410 | 870 | 1040 | 1170 | 3 X 1500 | 4500000 | 1575 | 1875 | 2115 | 1305 | 1560 | 1755
1750 | 1750000 | 545 | 650 | 735 | 455 | 545 | 615 | 2 X 1750 | 3500000 | 1090 | 1300 | 1470 | 910 | 1090 | 1230 | 3 X 1750 | 5250000 | 1635 | 1950 | 2205 | 1365 | 1635 | 1845
2000 | 2000000 | 555 | 665 | 750 | 470 | 560 | 630 | 2 X 2000 | 4000000 | 1110 | 1330 | 1500 | 940 | 1120 | 1260 | 3 X 2000 | 6000000 | 1665 | 1995 | 2250 | 1410 | 1680 | 1890
4 X 2 | 265440 | 4X | 4X | 4X | 4X | 4X | 4X | 5 X 2 | 331800 | 5X | 5X | 5X | 5X | 5X | 5X | 6 X 2 | 398160 | 6X | 6X | 6X | 6X | 6X | 6X
AWG | CMILS | 60C | 75C | 90C | 60C | 75C | 90C | AWG | CMILS | 60C | 75C | 90C | 60C | 75C | 90C | AWG | CMILS | 60C | 75C | 90C | 60C | 75C | 90C
4 X 1/O | 422400 | 500 | 600 | 680 | 400 | 480 | 540 | 5 X 1/O | 528000 | 625 | 750 | 850 | 500 | 600 | 675 | 6 X 1/O | 633600 | 750 | 900 | 1020 | 600 | 720 | 810
4 X 2/O | 532400 | 580 | 700 | 780 | 460 | 540 | 600 | 5 X 2/O | 665500 | 725 | 875 | 975 | 575 | 675 | 750 | 6 X 2/O | 798600 | 870 | 1050 | 1170 | 690 | 810 | 900
4 X 3/O | 671200 | 660 | 800 | 900 | 520 | 620 | 700 | 5 X 3/O | 839000 | 825 | 1000 | 1125 | 650 | 775 | 875 | 6 X 3/O | 1006800 | 990 | 1200 | 1350 | 780 | 930 | 1050
4 X 4/O | 846400 | 780 | 920 | 1040 | 600 | 720 | 820 | 5 X 4/O | 1058000 | 975 | 1150 | 1300 | 750 | 900 | 1025 | 6 X 4/O | 1269600 | 1170 | 1380 | 1560 | 900 | 1080 | 1230
4 X 250 | 1000000 | 860 | 1020 | 1160 | 680 | 820 | 920 | 5 X 250 | 1250000 | 1075 | 1275 | 1450 | 850 | 1025 | 1150 | 6 X 250 | 1500000 | 1290 | 1530 | 1740 | 1020 | 1230 | 1380
4 X 300 | 1200000 | 960 | 1140 | 1280 | 780 | 920 | 1040 | 5 X 300 | 1500000 | 1200 | 1425 | 1600 | 975 | 1150 | 1300 | 6 X 300 | 1800000 | 1440 | 1710 | 1920 | 1170 | 1380 | 1560
4 X 350 | 1400000 | 1040 | 1240 | 1400 | 840 | 1000 | 1120 | 5 X 350 | 1750000 | 1300 | 1550 | 1750 | 1050 | 1250 | 1400 | 6 X 350 | 2100000 | 1560 | 1860 | 2100 | 1260 | 1500 | 1680
4 X 400 | 1600000 | 1120 | 1340 | 1520 | 900 | 1080 | 1220 | 5 X 400 | 2000000 | 1400 | 1675 | 1900 | 1125 | 1350 | 1525 | 6 X 400 | 2400000 | 1680 | 2010 | 2280 | 1350 | 1620 | 1830
4 X 500 | 2000000 | 1280 | 1520 | 1720 | 1040 | 1240 | 1400 | 5 X 500 | 2500000 | 1600 | 1900 | 2150 | 1300 | 1550 | 1750 | 6 X 500 | 3000000 | 1920 | 2280 | 2580 | 1560 | 1860 | 2100
4 X 600 | 2400000 | 1400 | 1680 | 1900 | 1140 | 1360 | 1540 | 5 X 600 | 3000000 | 1750 | 2100 | 2375 | 1425 | 1700 | 1925 | 6 X 600 | 3600000 | 2100 | 2520 | 2850 | 1710 | 2040 | 2310
4 X 700 | 2800000 | 1540 | 1840 | 2080 | 1260 | 1500 | 1700 | 5 X 700 | 3500000 | 1925 | 2300 | 2600 | 1575 | 1875 | 2125 | 6 X 700 | 4200000 | 2310 | 2760 | 3120 | 1890 | 2250 | 2550
4 X 750 | 3000000 | 1600 | 1900 | 2140 | 1280 | 1540 | 1740 | 5 X 750 | 3750000 | 2000 | 2375 | 2675 | 1600 | 1925 | 2175 | 6 X 750 | 4500000 | 2400 | 2850 | 3210 | 1920 | 2310 | 2610
4 X 800 | 3200000 | 1640 | 1960 | 2220 | 1320 | 1580 | 1780 | 5 X 800 | 4000000 | 2050 | 2450 | 2775 | 1650 | 1975 | 2225 | 6 X 800 | 4800000 | 2460 | 2940 | 3330 | 1980 | 2370 | 2670
4 X 900 | 3600000 | 1740 | 2080 | 2340 | 1420 | 1700 | 1920 | 5 X 900 | 4500000 | 2175 | 2600 | 2925 | 1775 | 2125 | 2400 | 6 X 900 | 5400000 | 2610 | 3120 | 3510 | 2130 | 2550 | 2880
4 X 1000 | 4000000 | 1820 | 2180 | 2460 | 1500 | 1780 | 2000 | 5 X 1000 | 5000000 | 2275 | 2725 | 3075 | 1875 | 2225 | 2500 | 6 X 1000 | 6000000 | 2730 | 3270 | 3690 | 2250 | 2670 | 3000
4 X 1250 | 5000000 | 1980 | 2360 | 2660 | 1620 | 1940 | 2180 | 5 X 1250 | 6250000 | 2475 | 2950 | 3325 | 2025 | 2425 | 2725 | 6 X 1250 | 7500000 | 2970 | 3540 | 3990 | 2430 | 2910 | 3270
4 X 1500 | 6000000 | 2100 | 2500 | 2820 | 1740 | 2080 | 2340 | 5 X 1500 | 7500000 | 2625 | 3125 | 3525 | 2175 | 2600 | 2925 | 6 X 1500 | 9000000 | 3150 | 3750 | 4230 | 2610 | 3120 | 3510
4 X 1750 | 7000000 | 2180 | 2600 | 2940 | 1820 | 2180 | 2460 | 5 X 1750 | 8750000 | 2725 | 3250 | 3675 | 2275 | 2725 | 3075 | 6 X 1750 | 10500000 | 3270 | 3900 | 4410 | 2730 | 3270 | 3690
4 X 2000 | 8000000 | 2220 | 2660 | 3000 | 1880 | 2240 | 2520 | 5 X 2000 | 10000000 | 2775 | 3325 | 3750 | 2350 | 2800 | 3150 | 6 X 2000 | 12000000 | 3330 | 3990 | 4500 | 2820 | 3360 | 3780

## Field VD
POWER DROP TO WELL CALCULATION
|  |  |  | K |  |  |  |  | CALC. | ACTUAL | ACTUAL | CALC. WELL
TO | SOURCE | LENGTH | 1.732 or 2 | 21.2 OR 12.9 | AMPS | PD VOLTS | MAX %VD | VD | Cmils | Wire Size | Cmils | HEAD VOLTS
WELL 1 | PD1 | 4000 | 1.732 | 21.2 | 45 | 460 | 3% | 13.8 | 478935.6522 | 2 x 250 | 500000 | 446.7814
WELL 2 | PD1 | 2000 | 1.732 | 21.2 | 25 | 460 | 3% | 13.8 | 133037.6812 | 250 | 250000 | 452.6563
WELL 3 | PD1 | 2500 | 1.732 | 21.2 | 50 | 460 | 3% | 13.8 | 332594.2029 | 2 x 250 | 500000 | 450.8204
WELL 4 | PD2 | 1000 | 1.732 | 21.2 | 25 | 460 | 3% | 13.8 | 66518.8406 | 250 | 250000 | 456.3282
WELL 5 | PD3 | 500 | 1.732 | 21.2 | 25 | 460 | 3% | 13.8 | 33259.4203 | 250 | 250000 | 458.1641
SURFACE TO PUMP CALCULATION
DOWN HOLE |  | K | [5 empty] | ACTUAL
LENGTH | 1.732 or 2 | 21.2 OR 12.9 | AMPS | MAX DROP | VD | Cmils | DH WIRE | Cmils | DH VOLTS | T. %VD | TO | SOURCE
1000 | 1.732 | 12.9 | 45 | 5% | 22.3391 | 45007.5162 | 8 | 16510 | 385.8834 | 16.11% | WELL 1 | PD1
1000 | 1.732 | 12.9 | 25 | 5% | 22.6328 | 24679.651 | 8 | 16510 | 418.8241 | 8.951% | WELL 2 | PD1
1000 | 1.732 | 12.9 | 50 | 5% | 22.541 | 49560.3127 | 8 | 16510 | 383.156 | 16.71% | WELL 3 | PD1
1000 | 1.732 | 12.9 | 25 | 5% | 22.8164 | 24481.0664 | 8 | 16510 | 422.4959 | 8.153% | WELL 4 | PD2
1000 | 1.732 | 12.9 | 25 | 5% | 22.9082 | 24382.9678 | 8 | 16510 | 424.3319 | 7.754% | WELL 5 | PD3
| 3 Phase, 460 | 1 Phase, 230 |  |  |  | AWG | Cmils
HP | Load | Load |  |  |  | 18 | 1620
2 | 3.4 | 12 |  |  |  | 16 | 2580
3 | 4.8 | 17 |  |  |  | 14 | 4110
5 | 7.6 | 28 |  |  |  | 12 | 6530
7.5 | 11 | 40 |  |  |  | 10 | 10380
10 | 14 | 50 |  |  |  | 8 | 16510
15 | 21 |  |  |  |  | 6 | 26240
20 | 27 |  |  |  |  | 4 | 41740
25 | 34 |  |  |  |  | 3 | 52620
30 | 40 |  |  |  |  | 2 | 66360
40 | 52 |  |  |  |  | 1 | 83690 | X2 | X3
50 | 65 |  |  |  |  | 1/O | 105600 | 211200 | 316800
[6 empty] | 2/O | 133100 | 266200 | 399300
| -10% | -5 % | +5 % | +10 % |  | 3/O | 167800 | 335600 | 503400
110 | 99 | 104.5 | 115.5 | 121 |  | 4/O | 211600 | 423200 | 634800
120 | 108 | 114 | 126 | 132 |  | 250 | 250000 | 500000 | 750000
230 | 207 | 218.5 | 241.5 | 253 |  | 400 | 400000 | 800000 | 1200000
240 | 216 | 228 | 252 | 264 |  | 500 | 500000 | 1000000 | 1500000
460 | 414 | 437 | 483 | 506
480 | 432 | 456 | 504 | 528
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## CMIL
CALCULATED MINIMUM CMILS BASED ON VOLTAGE DROP | [13 empty] | 2016-10-27
Phase | 1.732 | Use 1.73 or 2
K | 21.2 | Use 21.2 for AL, or 12.9 for CU
Volts | 480 | Use the actual voltage at the power drop
%VD | 5% | Max Percent Voltage Drop | [5 empty] | 24 | Voltage Drop
HP Ref. | Load | 150 | 250 | 500 | 750 | 1000 | 1500 | 2000 | 2500 | 3000 | 3500 | 4000 | 4500 | 5000 | 5280
5 | 7.6 | 1744.124 | 2906.8733 | 5813.7467 | 8720.62 | 11627.4933 | 17441.24 | 23254.9867 | 29068.7333 | 34882.48 | 40696.2267 | 46509.9733 | 52323.72 | 58137.4667 | 61393.1648
7.5 | 11 | 2524.39 | 4207.3167 | 8414.6333 | 12621.95 | 16829.2667 | 25243.9 | 33658.5333 | 42073.1667 | 50487.8 | 58902.4333 | 67317.0667 | 75731.7 | 84146.3333 | 88858.528
10 | 14 | 3212.86 | 5354.7667 | 10709.5333 | 16064.3 | 21419.0667 | 32128.6 | 42838.1333 | 53547.6667 | 64257.2 | 74966.7333 | 85676.2667 | 96385.8 | 107095.3333 | 113092.672
15 | 21 | 4819.29 | 8032.15 | 16064.3 | 24096.45 | 32128.6 | 48192.9 | 64257.2 | 80321.5 | 96385.8 | 112450.1 | 128514.4 | 144578.7 | 160643 | 169639.008
20 | 27 | 6196.23 | 10327.05 | 20654.1 | 30981.15 | 41308.2 | 61962.3 | 82616.4 | 103270.5 | 123924.6 | 144578.7 | 165232.8 | 185886.9 | 206541 | 218107.296
25 | 34 | 7802.66 | 13004.4333 | 26008.8667 | 39013.3 | 52017.7333 | 78026.6 | 104035.4667 | 130044.3333 | 156053.2 | 182062.0667 | 208070.9333 | 234079.8 | 260088.6667 | 274653.632
30 | 40 | 9179.6 | 15299.3333 | 30598.6667 | 45898 | 61197.3333 | 91796 | 122394.6667 | 152993.3333 | 183592 | 214190.6667 | 244789.3333 | 275388 | 305986.6667 | 323121.92
40 | 52 | 11933.48 | 19889.1333 | 39778.2667 | 59667.4 | 79556.5333 | 119334.8 | 159113.0667 | 198891.3333 | 238669.6 | 278447.8667 | 318226.1333 | 358004.4 | 397782.6667 | 420058.496
50 | 65 | 14916.85 | 24861.4167 | 49722.8333 | 74584.25 | 99445.6667 | 149168.5 | 198891.3333 | 248614.1667 | 298337 | 348059.8333 | 397782.6667 | 447505.5 | 497228.3333 | 525073.12
| 10 | 2294.9 | 3824.8333 | 7649.6667 | 11474.5 | 15299.3333 | 22949 | 30598.6667 | 38248.3333 | 45898 | 53547.6667 | 61197.3333 | 68847 | 76496.6667 | 80780.48
AWG | Cmils |  |  |  | Warning: | Don't forget to calculate your minimum wire size first!
18 | 1620 |  |  |  |  | See 210.19 (A)(1), 215.2(A), and 430.22
16 | 2580
14 | 4110
12 | 6530
10 | 10380
8 | 16510
6 | 26240
4 | 41740
3 | 52620
2 | 66360
1 | 83690 | X2 | X3
1/O | 105600 | 211200 | 316800
2/O | 133100 | 266200 | 399300
3/O | 167800 | 335600 | 503400 |  | Spreadsheet by:
4/O | 211600 | 423200 | 634800 |  | Lorn Macilravie, Master Electrician
250 | 250000 | 500000 | 750000 |  | risingedgeservices@gmail.com
400 | 400000 | 800000 | 1200000 |  | Mobile: 307-696-7926
500 | 500000 | 1000000 | 1500000 |  | The YELLOW cells are not protected.
1.732
2
21.2
12.9

## VD
Voltage Drop Calculator
480 | Volts | AWG | CMILS
150 | Amperes | 18 | 1620
1500 | Distance (Feet) | 16 | 2580
250000 | CMILS | 14* | 4110
|  | 12* | 6530
|  | 10* | 10380
4.184% | Percent Voltage Drop, CU, 3 Phase | 8 | 16510
20.0853 | Volts Dropped, CU, 3 Phase | 6 | 26240
459.9147 | Volts (Out) | 4 | 41740
|  | 3 | 52620
6.877% | Percent Voltage Drop, AL, 3 Phase | 2 | 66360
33.0084 | Volts Dropped, AL, 3 Phase | 1 | 83690
446.9916 | Volts (Out) | 1/O | 105600
|  | 2/O | 133100
4.837% | Percent Voltage Drop, CU, Single Phase | 3/O | 167800
23.22 | Volts Dropped, CU, Single Phase | 4/O | 211600
456.78 | Volts (Out) | 250 | 250000
7.95% | Percent Voltage Drop, AL, Single Phase
38.16 | Volts Dropped, AL, Single Phase
441.84 | Volts (Out)
K=12.9 for CU and K=21.2 for AL
1.73 X I X L X K / Cmils = VD 3 Phase
2 X I X L X K / Cmils = VD Single Phase
( VD / E ) x 100 = %VD
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## Z
Percent VD for 3 Phase Cables at 0.85 PF at 75C
Volts | 480 | Use the actual voltage at the power drop
Amps | 100 | Use actual load
| Z | 90 | 250 | 500 | 750 | 1000 | 1250 | 1500 | 1750 | 2000 | 2250 | 2500 | 3000 | 3500 | 4000 | 4500 | 5000 | 5280 | FEET
#1 | 0.24 | 0.7794% | 2.165% | 4.33% | 6.495% | 8.66% | 10.82% | 12.99% | 15.15% | 17.32% | 19.49% | 21.65% | 25.98% | 30.31% | 34.64% | 38.97% | 43.3% | 45.72%
1/O | 0.19 | 0.617% | 1.714% | 3.428% | 5.142% | 6.856% | 8.57% | 10.28% | 12% | 13.71% | 15.43% | 17.14% | 20.57% | 24% | 27.42% | 30.85% | 34.28% | 36.2%
2/O | 0.16 | 0.5196% | 1.443% | 2.887% | 4.33% | 5.773% | 7.217% | 8.66% | 10.1% | 11.55% | 12.99% | 14.43% | 17.32% | 20.21% | 23.09% | 25.98% | 28.87% | 30.48%
3/O | 0.13 | 0.4222% | 1.173% | 2.345% | 3.518% | 4.691% | 5.864% | 7.036% | 8.209% | 9.382% | 10.55% | 11.73% | 14.07% | 16.42% | 18.76% | 21.11% | 23.45% | 24.77%
4/O | 0.11 | 0.3572% | 0.9923% | 1.985% | 2.977% | 3.969% | 4.961% | 5.954% | 6.946% | 7.938% | 8.931% | 9.923% | 11.91% | 13.89% | 15.88% | 17.86% | 19.85% | 20.96%
250 | 0.094 | 0.3053% | 0.848% | 1.696% | 2.544% | 3.392% | 4.24% | 5.088% | 5.936% | 6.784% | 7.632% | 8.48% | 10.18% | 11.87% | 13.57% | 15.26% | 16.96% | 17.91%
300 | 0.082 | 0.2663% | 0.7397% | 1.479% | 2.219% | 2.959% | 3.699% | 4.438% | 5.178% | 5.918% | 6.657% | 7.397% | 8.877% | 10.36% | 11.84% | 13.31% | 14.79% | 15.62%
350 | 0.073 | 0.2371% | 0.6585% | 1.317% | 1.976% | 2.634% | 3.293% | 3.951% | 4.61% | 5.268% | 5.927% | 6.585% | 7.902% | 9.219% | 10.54% | 11.85% | 13.17% | 13.91%
400 | 0.066 | 0.2143% | 0.5954% | 1.191% | 1.786% | 2.381% | 2.977% | 3.572% | 4.168% | 4.763% | 5.358% | 5.954% | 7.145% | 8.335% | 9.526% | 10.72% | 11.91% | 12.57%
500 | 0.057 | 0.1851% | 0.5142% | 1.028% | 1.543% | 2.057% | 2.571% | 3.085% | 3.599% | 4.114% | 4.628% | 5.142% | 6.17% | 7.199% | 8.227% | 9.255% | 10.28% | 10.86%
600 | 0.051 | 0.1656% | 0.4601% | 0.9201% | 1.38% | 1.84% | 2.3% | 2.76% | 3.22% | 3.681% | 4.141% | 4.601% | 5.521% | 6.441% | 7.361% | 8.281% | 9.201% | 9.717%
750 | 0.045 | 0.1461% | 0.4059% | 0.8119% | 1.218% | 1.624% | 2.03% | 2.436% | 2.842% | 3.247% | 3.653% | 4.059% | 4.871% | 5.683% | 6.495% | 7.307% | 8.119% | 8.573%
1000 | 0.039 | 0.1267% | 0.3518% | 0.7036% | 1.055% | 1.407% | 1.759% | 2.111% | 2.463% | 2.814% | 3.166% | 3.518% | 4.222% | 4.925% | 5.629% | 6.333% | 7.036% | 7.43%
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## HP KVA KW
ELECTRICAL CALCULATIONS
[5 empty] | 480 | E (Volts)
Amperes = | HP X 746 | = | 526.3841 | Amperes
| E X % EFF X PF X (1.73 or 1) |  |  |  | 0.8 | PF (Power Factor)
[5 empty] | 80% | % EFF (Efficiency)
Amperes = | kW X 1000 | = | 180.6358 | Amperes | 375 | HP (Horsepower)
E X PF X (1.73 or 1)
[5 empty] | 120 | KW (Kilowatts)
[5 empty] | 120 | KVA ( Kilo-volt Amperes)
Amperes = | kVA X 1000 | = | 144.5087 | Amperes
| E X (1.73 or 1) |  |  |  | 180 | I (Amperes)
[5 empty] | 1.73 | 1.73 or 1
(Use 1.73 for 3 Phase and 1 for Single Phase)
KW = | E X I X PF X (1.73 or 1) | = | 119.5776 | Kilowatts
1000
KVA = | E x I x (1.73 or 1) | = | 149.472 | kVA
1000
HP = | E x I x %EFF x PF x (1.73 or 1) | = | 128.2334 | Horsepower
746
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## Ohm s Law
Ohms Law Calculator | [8 empty] | 2016-11-02
120 | E (Volts)
Place your values in these boxes. These values are plugged into the formulas below and automatically calculated.
12 | R (Ohms)
10 | I (Amps)
1200 | P (Watts)
Amps = | √ (Watts / Ohms) | = | 10 |  | Volts = | √ (Watts x Ohms) | = | 120
Amps = | Watts | = | 10 |  | Volts = | Amps x Ohms | = | 120
Volts
Amps = | Volts | = | 10 |  | Volts = | Watts | = | 120
| Ohms |  |  |  |  | Amps
Watts = | Volts2 | = | 1200 |  | Ohms = | Volts2 | = | 12
| Ohms |  |  |  |  | Watts
Watts = | Volts x Amps | = | 1200 |  | Ohms = | Watts | = | 12
Amps2
Watts = | Amps2 x Ohms | = | 1200 |  | Ohms = | Volts | = | 12
Amps
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## SC Calc.
Three Phase Voltage Drop and Short Circuit Calculator
Transformer
Power Drop
K= 12.9 CU or 21.2 AL | 12.9
[11 empty] | AWG | Cmils
Length | 20 |  | Cmils Segment 1 | 500000 | Cmils Segment 2 | 250000 | Cmils Segment 3 | 250000 | Cmils Segment 4 | 250000 | 13.0040740740733 | 4110
|  |  | Length Segment 1 | 250 | Length Segment 2 | 350 | Length Segment 3 | 3000 | Length Segment 4 | 2500 | 11.0040740740733 | 6530
L-L Volts | 470 |  | Motor Amps Panel 1 | 8 | Motor Amps Panel 2 | 11.5 | Motor Amps Panel 3 | 8 | Motor Amps Panel 4 | 8 | 9.00407407407329 | 10380
|  |  | Resistive Amps Panel 1 | 2 | Resistive Amps Panel 2 | 0 | Resistive Amps Panel 3 | 0 | Resistive Amps Panel 4 | 0
kVA | 150 |  | Total Amps Segment 1 | 37.5 | Total Amps Segment 2 | 27.5 | Total Amps Segment 3 | 16 | Total Amps Segment 4 | 8 | 7.00407407407329 | 16510
|  |  | Voltage at Panel 1 | 469.5811 | Voltage at Panel 2 | 468.7209 | Voltage at Panel 3 | 464.4311 | Voltage at Panel 4 | 462.6436 | 5.00407407407329 | 26240
% Z | 1.3 |  | % Voltage Drop from PCC | 0.08913% | % Voltage Drop from PCC | 0.2722% | % Voltage Drop from PCC | 1.185% | % Voltage Drop from PCC | 1.565% | 3.00407407407329 | 41740
[11 empty] | 2 | 52620
| Point of Common Coupling (PCC) |  | Segment 1 |  | Segment 2 |  | Segment 3 |  | segment 4 |  | 1 | 83690
|  |  |  | PANEL 1 |  | PANEL 2 |  | PANEL 3 |  | PANEL 4 | 1/0 | 105600
[11 empty] | 2/0 | 133100
Total I s.c. sym RMS | 13562.2779 |  | Total I s.c. sym RMS | 8199.5011 | Total I s.c. sym RMS | 5305.5084 | Total I s.c. sym RMS | 1399.2413 | Total I s.c. sym RMS | 911.9608 | 3/0 | 167800
[11 empty] | 4/0 | 211600
"C" Value | 18593 |  | "C" Value | 18593 | "C" Value | 18593 | "C" Value | 18593 | "C" Value | 18593 | 250 | 250000
Conductors per phase | 1 |  | Conductors per phase | 1 | Conductors per phase | 1 | Conductors per phase | 1 | Conductors per phase | 1
CALCULATION REFERENCE AREA
3 Phase | 1.732
FLA | 184.2661
Multiplier | 76.9231
I s.c. at Transformer | 14174.3176 |  | Available I s.c. | 13420.2779 | Available I s.c. | 8057.5011 | Available I s.c. | 5163.5084 | Available I s.c. | 1257.2413
"f" | 0.056187 |  | "f" | 0.66556 | "f" | 0.56047 | "f" | 3.107 | "f" | 0.63286
M | 0.9468 |  | M | 0.6004 | M | 0.64083 | M | 0.24349 | M | 0.61242
I s.c. sym RMS | 13420.2779 |  | I s.c. sym RMS | 8057.5011 | I s.c. sym RMS | 5163.5084 | I s.c. sym RMS | 1257.2413 | I s.c. sym RMS | 769.9608
Total Motor Amps | 35.5 |  | Total Motor Amps | 35.5 | Total Motor Amps | 35.5 | Total Motor Amps | 35.5 | Total Motor Amps | 35.5
I s.c Motor Contribution | 142 |  | I s.c Motor Contribution | 142 | I s.c Motor Contribution | 142 | I s.c Motor Contribution | 142 | I s.c Motor Contribution | 142
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.
This calculator is based on the information in Ugly's Electrical References.
You can find information on the wire sizes and the "C" value in the Ugly's Electrical References, or in publications from Cooper Bussmann.

## MAX CAPS
MAX CAPACITOR SIZES FOR 3 PHASE, 60HZ, MOTORS
|  | 3600 RPM |  | 1800 RPM |  | 1200 RPM
Motor Rating HP | KW | Maximum Capacitor Rating KVAR | Reduction In Line Current % | Maximum Capacitor Rating KVAR | Reduction In Line Current % | Maximum Capacitor Rating KVAR | Reduction In Line Current %
10 | 7.46 | 3 | 10 | 3 | 11 | 3.5 | 14
15 | 11.19 | 4 | 9 | 4 | 10 | 5 | 13
20 | 14.92 | 5 | 9 | 5 | 10 | 6.5 | 12
25 | 18.65 | 6 | 9 | 6 | 10 | 7.5 | 11
30 | 22.38 | 7 | 8 | 7 | 9 | 9 | 11
40 | 29.84 | 9 | 8 | 9 | 9 | 11 | 10
50 | 37.3 | 12 | 8 | 11 | 9 | 13 | 10
60 | 44.76 | 14 | 8 | 14 | 8 | 15 | 10
75 | 55.95 | 17 | 8 | 16 | 8 | 18 | 10
100 | 74.6 | 22 | 8 | 21 | 8 | 25 | 9
125 | 93.25 | 27 | 8 | 26 | 8 | 30 | 9
150 | 111.9 | 32.5 | 8 | 30 | 8 | 35 | 9
200 | 149.2 | 40 | 8 | 37.5 | 8 | 42.5 | 9
|  | 900 RPM |  | 720 RPM |  | 600 RPM
Motor Rating HP | KW | Maximum Capacitor Rating KVAR | Reduction In Line Current % | Maximum Capacitor Rating KVAR | Reduction In Line Current % | Maximum Capacitor Rating KVAR | Reduction In Line Current %
10 | 7.46 | 5 | 21 | 6.5 | 27 | 7.5 | 31
15 | 11.19 | 6.5 | 18 | 8 | 23 | 9.5 | 27
20 | 14.92 | 7.5 | 16 | 9 | 21 | 12 | 25
25 | 18.65 | 9 | 15 | 11 | 20 | 12 | 23
30 | 22.38 | 10 | 14 | 12 | 18 | 14 | 22
40 | 29.84 | 12 | 13 | 15 | 16 | 20 | 20
50 | 37.3 | 15 | 12 | 19 | 15 | 24 | 19
60 | 44.76 | 18 | 11 | 22 | 15 | 27 | 19
75 | 55.95 | 21 | 10 | 26 | 14 | 32.5 | 18
100 | 74.6 | 27 | 10 | 32.5 | 13 | 40 | 17
125 | 93.25 | 32.5 | 10 | 40 | 13 | 47.5 | 16
150 | 111.9 | 37.5 | 10 | 47.5 | 12 | 52.5 | 15
200 | 149.2 | 47.5 | 10 | 60 | 12 | 65 | 14

## Cap. Calc.
POWER FACTOR CORRECTION
Based on Table in Ugly's Electrical Reference, 2011 Edition, Page 27
55 | KW
Existing PF | Corrected Power Factor
| 1 | 0.95 | 0.9 | 0.85 | 0.8 | 0.75
0.5 | 95.26 | 77.165 | 68.585 | 61.16 | 54.01 | 46.75
0.52 | 90.365 | 72.27 | 63.69 | 56.265 | 49.115 | 41.855
0.54 | 85.69 | 67.595 | 59.015 | 51.59 | 44.44 | 37.18
0.55 | 83.49 | 65.395 | 56.815 | 49.39 | 42.24 | 34.98
0.56 | 81.345 | 63.25 | 54.67 | 47.245 | 40.095 | 32.835
0.58 | 77.22 | 59.125 | 50.545 | 43.12 | 35.97 | 28.71
0.6 | 73.315 | 55.22 | 46.64 | 39.215 | 32.065 | 24.805
0.62 | 69.575 | 51.48 | 42.9 | 35.475 | 28.325 | 21.065
0.64 | 66.055 | 47.96 | 39.38 | 31.955 | 24.805 | 17.545
0.65 | 64.24 | 46.145 | 37.565 | 30.14 | 22.99 | 15.73
0.66 | 62.645 | 44.55 | 35.97 | 28.545 | 21.395 | 14.135
0.68 | 59.29 | 41.195 | 32.615 | 25.19 | 18.04 | 10.78
0.7 | 56.1 | 38.005 | 29.425 | 22 | 14.85 | 7.59
0.72 | 53.02 | 34.925 | 26.345 | 18.92 | 11.77 | 4.51
0.74 | 49.995 | 31.9 | 23.32 | 15.895 | 8.745 | 1.485
0.75 | 48.51 | 30.415 | 21.835 | 14.41 | 7.26
0.76 | 47.025 | 28.93 | 20.35 | 12.925 | 5.775
0.78 | 44.11 | 24.035 | 17.435 | 10.01 | 2.86
0.8 | 41.25 | 23.155 | 14.575 | 7.15
0.82 | 38.39 | 20.295 | 11.715 | 4.29
0.84 | 35.2 | 17.435 | 8.855
0.85 | 34.1 | 16.005 | 7.425
0.86 | 32.67 | 14.575 | 5.995
0.88 | 29.7 | 11.605 | 3.025
0.9 | 26.675 | 8.58
0.92 | 23.43 | 5.335
0.94 | 19.965 | 1.87
0.95 | 18.095
0.7 | Existing PF
0.95 | Desired PF
38.0336 | kVAR of PF Capacitor required to change PF from "Existing PF" to "Desired PF"
0.69152 | Table Value
29.4735 | Existing PF Corrected to 0.90
31.0525 | Existing PF Corrected to 0.91
32.6813 | Existing PF Corrected to 0.92
34.3738 | Existing PF Corrected to 0.93
36.1489 | Existing PF Corrected to 0.94
38.0336 | Existing PF Corrected to 0.95
40.0696 | Existing PF Corrected to 0.96
42.3269 | Existing PF Corrected to 0.97
44.943 | Existing PF Corrected to 0.98
48.2741 | Existing PF Corrected to 0.99
56.1112 | Existing PF Corrected to 0.100

## Bends
DISTANCE BETWEEN BENDS | [8 empty] | 2016-11-02
COSECANT | 5.76 | 2.6 | 2 | 1.414 | 1.15
ANGLE | 10 | 22.5 | 30 | 45 | 60 | DEGREES
1 | 5.76 | 2.6 | 2 | 1.414 | 1.15
1.5 | 8.64 | 3.9 | 3 | 2.121 | 1.725 |  | ONE SHOTS
2 | 11.52 | 5.2 | 4 | 2.828 | 2.3 |  | ONE SHOT | TAKE UP | SHRINK
2.5 | 14.4 | 6.5 | 5 | 3.535 | 2.875 |  | 1/2 | 5 | 3/16
3 | 17.28 | 7.8 | 6 | 4.242 | 3.45 |  | 3/4 | 6 | 1/4
3.5 | 20.16 | 9.1 | 7 | 4.949 | 4.025 |  | 1 | 8 | 3/8
4 | 23.04 | 10.4 | 8 | 5.656 | 4.6 |  | 1 1/4 | 11 | 1/2
4.5 | 25.92 | 11.7 | 9 | 6.363 | 5.175
5 | 28.8 | 13 | 10 | 7.07 | 5.75 |  | SADDLES
5.5 | 31.68 | 14.3 | 11 | 7.777 | 6.325 |  | DEPTH | ADD | DISTANCE
6 | 34.56 | 15.6 | 12 | 8.484 | 6.9 |  | 1 | 3/16 | 2.5
6.5 | 37.44 | 16.9 | 13 | 9.191 | 7.475 |  | 2 | 3/8 | 5
7 | 40.32 | 18.2 | 14 | 9.898 | 8.05 |  | 3 | 9/16 | 7.5
7.5 | 43.2 | 19.5 | 15 | 10.605 | 8.625 |  | 4 | 3/4 | 10
8 | 46.08 | 20.8 | 16 | 11.312 | 9.2 |  | 5 | 15/16 | 12.5
8.5 | 48.96 | 22.1 | 17 | 12.019 | 9.775 |  | 6 | 1-1/8 | 15
9 | 51.84 | 23.4 | 18 | 12.726 | 10.35
9.5 | 54.72 | 24.7 | 19 | 13.433 | 10.925
10 | 57.6 | 26 | 20 | 14.14 | 11.5
10.5 | 60.48 | 27.3 | 21 | 14.847 | 12.075
11 | 63.36 | 28.6 | 22 | 15.554 | 12.65
11.5 | 66.24 | 29.9 | 23 | 16.261 | 13.225
12 | 69.12 | 31.2 | 24 | 16.968 | 13.8
12.5 | 72 | 32.5 | 25 | 17.675 | 14.375
13 | 74.88 | 33.8 | 26 | 18.382 | 14.95
13.5 | 77.76 | 35.1 | 27 | 19.089 | 15.525
14 | 80.64 | 36.4 | 28 | 19.796 | 16.1
14.5 | 83.52 | 37.7 | 29 | 20.503 | 16.675
15 | 86.4 | 39 | 30 | 21.21 | 17.25
15.5 | 89.28 | 40.3 | 31 | 21.917 | 17.825
16 | 92.16 | 41.6 | 32 | 22.624 | 18.4
16.5 | 95.04 | 42.9 | 33 | 23.331 | 18.975
17 | 97.92 | 44.2 | 34 | 24.038 | 19.55
17.5 | 100.8 | 45.5 | 35 | 24.745 | 20.125
18 | 103.68 | 46.8 | 36 | 25.452 | 20.7
18.5 | 106.56 | 48.1 | 37 | 26.159 | 21.275
19 | 109.44 | 49.4 | 38 | 26.866 | 21.85
19.5 | 112.32 | 50.7 | 39 | 27.573 | 22.425
20 | 115.2 | 52 | 40 | 28.28 | 23
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## 777
Franklin Electric HP | HP | 2 | 3 | 5 | 7 1/2 | 10 | 15 | 20 | 25 | 30 | 40 | 50
|  | 4" | 4" | 4" | 4" | 4" | 6" | 6" | 6" | 6" | 6" | 6"
Franklin Full Load Amps | FLA | 3.5 | 4.9 | 8 | 11.8 | 17 | 20.8 | 26.9 | 33.5 | 39.5 | 53.5 | 67.7
Franklin Service Factor Amps | SFA | 4.1 | 5.4 | 8.9 | 13 | 18.5 | 23.7 | 30.3 | 37.5 | 45.2 | 62 | 77
NEC AMPS |  | 3.4 | 4.8 | 7.6 | 11 | 14 | 21 | 27 | 34 | 40 | 52 | 65
Low Voltage | LV | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450
High Voltage | HV | 506 | 506 | 506 | 506 | 506 | 506 | 506 | 506 | 506 | 506 | 506
Voltage Unbalance | VUB | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Loops "Multiplier" | MULT | 8 | 6 | 4 | 3 | 2 | 2 | 1 | 1 | 1 | 1 | 1
OC 115% RECOMMENDED | OC | 4.025 | 5.635 | 9.2 | 13.57 | 19.55 | 23.92 | 30.935 | 38.525 | 45.425 | 61.525 | 77.855
UC 85% | UC | 2.975 | 4.165 | 6.8 | 10.03 | 14.45 | 17.68 | 22.865 | 28.475 | 33.575 | 45.475 | 57.545
Current Unbalance | CUB | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Trip Class | TC | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Rapid Cycle Timer | RD1 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
Fault Restart Delay | RD2 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
UC Restart Delay Timer | RD3 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
# of Automatic Restarts | #RU | A | A | A | A | A | A | A | A | A | A | A
Address | ADDR | A01 | A01 | A01 | A01 | A01 | A01 | A01 | A01 | A01 | A01 | A01
# of Restarts after Faults | #RF | oc4 | oc4 | oc4 | oc4 | oc4 | oc4 | oc4 | oc4 | oc4 | oc4 | oc4
UC Trip Delay | UCTD | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Ground Fault 10% | GF | 0.35 | 0.49 | 0.8 | 1.18 | 1.7 | 2.08 | 2.69 | 3.35 | 3.95 | 5.35 | 6.77
HP |  | 2 | 3 | 5 | 7 1/2 | 10 | 15 | 20 | 25 | 30 | 40 | 50
# of conductors thru A, B, C |  | 8 | 6 | 4 | 3 | 2 | 2 | 1 | 1 | 1 | 1 | 1
Maximum NEC OC Settings | 125% | 4.375 | 6.125 | 10 | 14.75 | 21.25 | 26 | 33.625 | 41.875 | 49.375 | 66.875 | 84.625
Min. Wire Size @ 75C |  | 12 | 12 | 12 | 12 | 12 | 10 | 10 | 8 | 8 | 4 | 4
KW |  | 1.492 | 2.238 | 3.73 | 5.595 | 7.46 | 11.19 | 14.92 | 18.65 | 22.38 | 29.84 | 37.3
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## PSI SG
PSI, API, SG Calculator
p = 0.434 * h * SG
p | 7.2727 | PSI
h | 16 | Head in Feet
SG | 1.05 | Specific Gravity
h = (p * 2.31) / SG
p | 7.27 | PSI
h | 15.994 | Head in Feet
SG | 1.05 | Specific Gravity
API gravity = (141.5/SG at 60°F) - 131.5 |  |  | 30 | Light
|  |  | 22-30 | Medium
API | 45.375 |  | <22 | Heavy
SG | 0.8 |  | <10 | Extra Heavy
|  |  | 10 | Fresh Water
API | 45.38 |  | 8 | Asphalt
SG | 0.79998
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## Gas Laws
P1 | 13 | 14.73 | 13 | PSIA = PSIG + AVERAGE ATMOSPHERIC PRESSURE. Ex. AT 4500' ABOVE SEA LEVEL, USE (PSIG + 12.5 = PSIA)
V1 | 100 | 100 | 100 | UNITLESS VOLUME
T1 | 540 | 480 | 540 | ABSOLUTE TEMP = TEMP F + 460. Ex. 80F + 460 = 540 ABSOLUTE
P2 | 14.7277 | 14.73 | 14.73 | STANDARD PRESSURE IS 14.73 PSIA
V2 | 85 | 108.3333 | 85 | UNITLESS VOLUME
T2 | 520 | 520 | 520.0823 | STANDARD TEMPERATURE IS 520. Ex 520=460+60F
| (P1)(V1) | = | (P2)(V2)
| (T1) |  | (T2)
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## Solar
Optimal Solar Panel Tilt
46 | Latitude
70.4 | Desired Tilt | Latitude x 0.9 + 29° = Desired Tilt
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## API
A.P.I. | Specific Gravity | Wght. per Gal. | A.P.I. | Specific Gravity | Wght. per Gal.
10 | 1 | 8.33 | 55 | 0.7597 | 6.32
11 | 0.993 | 8.27 | 56 | 0.7556 | 6.28
12 | 0.986 | 8.21 | 57 | 0.7516 | 6.28
13 | 0.979 | 8.16 | 58 | 0.7476 | 6.22
14 | 0.973 | 8.1 | 59 | 0.7437 | 6.18
15 | 0.966 | 8.04 | 60 | 0.7398 | 6.15
16 | 0.959 | 7.99 | 61 | 0.7359 | 6.12
17 | 0.953 | 7.94 | 62 | 0.731 | 6.09
18 | 0.946 | 7.88 | 63 | 0.7283 | 6.06
19 | 0.94 | 7.83 | 64 | 0.7246 | 6.03
20 | 0.934 | 7.78 | 65 | 0.7209 | 5.99
21 | 0.928 | 7.73 | 66 | 0.7172 | 5.96
22 | 0.921 | 7.68 | 67 | 0.7136 | 5.93
23 | 0.916 | 7.63 | 68 | 0.709 | 5.9
24 | 0.91 | 7.58 | 69 | 0.7065 | 5.87
25 | 0.904 | 7.53 | 70 | 0.702 | 5.85
26 | 0.898 | 7.48 | 71 | 0.6995 | 5.82
27 | 0.893 | 7.43 | 72 | 0.695 | 5.79
28 | 0.887 | 7.39 | 73 | 0.6926 | 5.76
29 | 0.882 | 7.34 | 74 | 0.6893 | 5.73
30 | 0.876 | 7.3 | 75 | 0.6859 | 5.7
31 | 0.871 | 7.25 | 76 | 0.6826 | 5.68
32 | 0.865 | 7.21 | 77 | 0.6793 | 5.65
33 | 0.86 | 7.16 | 78 | 0.675 | 5.62
34 | 0.855 | 7.12 | 79 | 0.6728 | 5.6
35 | 0.85 | 7.08 | 80 | 0.6696 | 5.57
36 | 0.845 | 7.03 | 81 | 0.6665 | 5.54
37 | 0.84 | 6.99 | 82 | 0.6634 | 5.52
38 | 0.835 | 6.95 | 83 | 0.6603 | 5.49
39 | 0.83 | 6.91 | 84 | 0.6572 | 5.47
40 | 0.825 | 6.87 | 85 | 0.6541 | 5.44
41 | 0.82 | 6.83 | 86 | 0.6511 | 5.42
42 | 0.816 | 6.79 | 87 | 0.6481 | 5.39
43 | 0.811 | 6.75 | 88 | 0.6452 | 5.37
44 | 0.806 | 6.71 | 89 | 0.6422 | 5.34
45 | 0.802 | 6.68 | 90 | 0.6393 | 5.32
46 | 0.797 | 6.64 | 91 | 0.636 | 5.29
47 | 0.793 | 6.6 | 92 | 0.633 | 5.27
48 | 0.788 | 6.56 | 93 | 0.63 | 5.25
49 | 0.784 | 6.53 | 94 | 0.628 | 5.22
50 | 0.78 | 6.49 | 95 | 0.625 | 5.2
51 | 0.775 | 6.46 | 96 | 0.622 | 5.18
52 | 0.7712 | 6.42 | 97 | 0.619 | 5.15
53 | 0.767 | 6.39 | 98 | 0.617 | 5.13
54 | 0.7637 | 6.35 | 99 | 0.614 | 5.11
|  |  | 100 | 0.611 | 5.09

## Basic Motors
2011 and 2014 National Electrical Code Basic AC Motor Circuit Calculations
Find Full Load Current (FLC) in the appropriate table, 430.250 or 430.248.
Calculate Short Circuit and Ground Fault Protection
Use Table 430.52 first, then
Use Table 240.6 to find the Standard Ampere Rating.
Calculate the Conductor Size
Multiple the FLC by 125% as specified in 430.22.
Choose the correct conductor size using Table 310.15(B)(16)
Review 110.14(C)(1) to choose correct temperature rating.
Calculate the proper “Over Load” setting.
Look for Full Load Amperes (FLA) listed on the motor name plate.
Look for the Service Factor (SF) and/or Temperature Rise on the motor name plate.
Review 430.32(A)(1) to calculate the proper motor overload value.
Choose Minimum Equipment Grounding Conductor from Table 250.122.
Choose an appropriate conduit, cable, or cord for your motor circuit.
To calculate the correct conduit size using Tables 4 and 5 in Chapter 9, or use the Tables in Annex C.
Review Articles 320 to 340 for cable information.
Review Articles 342 to 362 for conduit information.
Review Article 400 for cord information
Choose the correct NEMA or IEC contactors and starter from equipment from information provided by manufactures. Review Article 100.3(B).
If you are using a variable speed drive, VSD, ASD, or a Soft Starter, read the information provided by the manufacturer carefully. Review Article 100.3(B).
Choose an appropriate enclosures, conduit, conduit fittings, and junction boxes. Base your selection on the location of the equipment.
Review Table 110.28.
Review Chapters 5-8, if the equipment will be used in Hazardous or Special Locations.
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
Mobile: 307-696-7926
The YELLOW cells are not protected.

## Standard Calc
1 | General Lighting and Receptacles, Small Appliances, and Laundry | [6 empty] | Work in Progress!
| Total Square Feet | 2700 | X | 3 | = | 8100 | VA | TABLE 220.12
| Small Appliance Circuits | 1500 | X | 2 | = | 3000 | VA | 220.52(A)
| Laundry Circuits | 1500 | X | 1 | = | 1500 | VA | 220.52(B)
| Total Connected Load |  |  |  |  | 12600 | VA
| First 3000 VA | 3000 | X | 1 | = | 3000 | VA | TABLE 220.42
| 3001 VA to 120000 VA | 9600 | X | 0.35 | = | 3360 | VA | TABLE 220.43
| Remainder | 0 | X | 0.25 | = | 0 | VA | TABLE 220.44
| Total #1 |  |  |  | Total Demand Load | 6360 | VA
2 | Air Conditioning or Heat | [6 empty] | 220.60
| Heating Calculations | 9000 | [5 empty] | 220.51
| Air Conditioning Calculations | 6440 | [5 empty] | 440.6 (A) and (B)
Use 100% of the total electric heating load. Use the Name Plate value for the AC loads.
| Total #2 | 9000 | VA
3 | Appliances | [6 empty] | 220.53
| Appliance 1 | 940 | [6 empty] | 3
| Appliance 2 | 1250
| Appliance 3 | 4500
| Appliance 4 | 0
| Appliance 5 | 0
Appliance 6
Appliance 7
Appliance 8
Appliance 9
Appliance 10
|  | 6690 | Total - Use this value, if there are 3 or fewer appliances
|  | 0.75 | X
|  | 5017.5 | Demand Factor applied (Total X 0.75) - Use this value if 4 or more appliances
| Total #3 | 6690 | VA
4 | Clothes Dryer | [6 empty] | 220.54
| Dryer VA | 4000
| Minimum VA | 5000
Use the name plate VA of your dryer, unless the nameplate is less than 5000 VA.
If less than 5000 VA, use 5000 VA for your dryer circuit.
| Total #4 | 5000 | VA
5 | Cooking Equipment | [6 empty] | TABLE 220.55
|  | Units | VA | Demand
| Column A | 0 | 3000 | 0.75 | 0 | VA
| Column B | 0 | 6000 | 0.8 | 0 | VA
| Column C |  |  |  | 8800 | VA
| Total #5 |  |  |  | 8800 | VA
6 | Motors | [6 empty] | 220.18(A) and 220.50
| Largest Motor VA | 0 | X 1.25 = | 0 | VA
| Sum of the other motor VA | 0 | X 1.00 = | 0 | VA
| Total #6 |  |  | 0 | VA
7 | Other Loads
| Load 1 | 0 | VA
| Load 2 | 0 | VA
|  | 0 | VA
8 | Feeder and Service Conductor Size
| Total #1 | 6360 | General Lighting and Receptacles, Small Appliances, and Laundry
| Total #2 | 9000 | Air Conditioning or Heat
| Total #3 | 6690 | Appliances
| Total #4 | 5000 | Clothes Dryer
| Total #5 | 8800 | Cooking Equipment
| Total #6 | 0 | Motors
| Total #7 | 0 | Other Loads
|  | 35850 | VA / 240 = | 149.375 | Amps
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
307-696-7926
The YELLOW cells are not protected.
Note on B10: GC-TEC: 38,500 Sq/Ft gives you 120,000 VA

## Optional Calc
Optional Method | [10 empty] | Work in Progress!
First Step: General Loads
| Load |  |  |  | Multiplier |  | Total
| Total Square Feet | 1500 | Sq./Ft. | X | 3 | = | 4500 | VA | 220.82(B)(1)
| Small Appliance Circuits | 1500 | VA | X | 2 | = | 3000 | VA | 220.82(B)(2)
| Laundry Circuits | 1500 | VA | X | 1 | = | 1500 | VA | 220.82(B)(2)
| Range NP Rating | 12000 | VA | X | 1 | = | 12000 | VA | 220.82(B)(3)
| Range NP Rating | 0 | VA | X | 1 | = | 0 | VA | 220.82(B)(3)
| Range NP Rating | 0 | VA | X | 1 | = | 0 | VA | 220.82(B)(3)
| Dryer NP Rating | 5000 | VA | X | 1 | = | 5000 | VA | 220.82(B)(3)
| Water Heater NP Rating | 4500 | VA | X | 1 | = | 4500 | VA | 220.82(B)(3)
| Appliance 1 | 1200 | VA | X | 1 | = | 1200 | VA | 220.82(B)(3)
| Appliance 2 | 4500 | VA | X | 1 | = | 4500 | VA | 220.82(B)(3)
| Appliance 3 | 900 | VA | X | 1 | = | 900 | VA | 220.82(B)(3)
| Appliance 4 | 450 | VA | X | 1 | = | 450 | VA | 220.82(B)(3)
| Appliance 5 | 200 | VA | X | 1 | = | 200 | VA | 220.82(B)(3)
| Appliance 6 |  | VA | X | 1 | = | 0 | VA | 220.82(B)(3)
| Appliance 7 |  | VA | X | 1 | = | 0 | VA | 220.82(B)(3)
| Appliance 8 |  | VA | X | 1 | = | 0 | VA | 220.82(B)(3)
| Appliance 9 |  | VA | X | 1 | = | 0 | VA | 220.82(B)(3)
| Appliance 10 |  | VA | X | 1 | = | 0 | VA | 220.82(B)(3)
| Motors |  | VA | X | 1 | = | 0 | VA | 220.82(B)(4)
| Motors |  | VA | X | 1 | = | 0 | VA | 220.82(B)(4)
| Other |  | VA | X | 1 | = | 0 | VA | 220.82(B)(4)
| Other |  | VA | X | 1 | = | 0 | VA | 220.82(B)(4)
| Total General Loads | [5 empty] | 37750 | VA
Second Step: Figure the Demand Load
[5 empty] | Multiplier |  | Total
| First 10,000 VA at 100% | 10000 | VA | X | 1 | = | 10000 | VA | 220.82(B)
| Remainder at 40%, ((Total Gen. Loads - First 10,000 VA at 100%) X 40%) | 27750 | VA | X | 0.4 | = | 11100 | VA | 220.82(B)
| Demand Load | [5 empty] | 21100 | VA
Third Step: Figure the LARGEST of six loads Heating and Air Conditioning Loads
[5 empty] | Multiplier |  | Subtotals |  | Totals
1 | Air Conditioning NP | 20000 | VA | X | 1 | = | 20000 | = | 20000 | VA | 220.82(C)(1) | Selection 1
2 | Heat Pump NP (Without Supplemental Heating) | 0 | VA | X | 1 | = | 0 | = | 0 | VA | 220.82(C)(2) | Selection 2
3.1 | Heat Pump NP (When used with Supplemental Heating) | 0 | VA | X | 1 | = | 0 |  |  |  | 220.82(C)(3) | Selection 3
3.2 | Heating Supplemental to the Heat Pump | 0 | VA | X | 0.65 | = | 0 | + |  |  | 220.82(C)(3) | Selection 3
3.3 | Total of Load 3 | [5 empty] | 0 | = | 0 | VA | Sum of | Selection 3
4 | 0 to 3 Space Heaters | 0 | VA | X | 0.65 | = | 0 | = | 0 | VA | 220.82(C)(4) | Selection 4
5 | 4 or more Space Heaters | 0 | VA | X | 0.4 | = | 0 | = | 0 | VA | 220.82(C)(5) | Selection 5
6 | Electric Thermal Storage | 0 | VA | X | 1 | = | 0 | = | 0 | VA | 220.82(C)(6) | Selection 6
| Heating and Air-Conditioning Load | [7 empty] | 20000 | VA | Largest of the Six Selections
Fourth Step: Add the Demand Load to the HVAC Load, then divide by 240V
| Demand Load |  |  |  |  | 21100
| Heating and Air-Conditioning Load |  |  |  |  | 20000
[6 empty] | 41100 | VA / 240 = | 171.25 | A
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
307-696-7926
The YELLOW cells are not protected.

## Winding Temp
Motor Winding Temperatures
20 | T1, First Temperature (Degrees Celsius) (Measure the cool, or cold, temperature before running the motor or transformer)
16 | R1, First Resistance (Ohms) (Measure at the same time you measure T1)
20 | R2, Second Resistance (Ohms) (Measured after running the motor or transformer)
63.6132 | T2, Second Temperature (Degrees Celsius) (CU windings, with a coefficient of 0.00393)
58.2751 | T2, Second Temperature (Degrees Celsius) (AL windings with a coefficient of 0.00429)
Formula used: ((R2/R1)-1)/coefficient
Celsius to Fahrenheit
37 | 98.6
Fahrenheit to Celsius
98.6 | 37
Spreadsheet by:
Lorn Macilravie, Master Electrician
risingedgeservices@gmail.com
307-696-7926
The YELLOW cells are not protected.

## KVA
MAX KVA AT 120 VAC, Single Phase, From Table 310.15 (B)(16) | [7 empty] | MAX KVA AT 240 VAC, Single Phase, From Table 310.15 (B)(16) | [7 empty] | MAX KVA AT 480 VAC, Single Phase, From Table 310.15 (B)(16)
| CU |  |  | AL |  |  |  |  | CU |  |  | AL |  |  |  |  | CU |  |  | AL
AWG | 60C | 75C | 90C | 60C | 75C | 90C | AWG | AWG | 60C | 75C | 90C | 60C | 75C | 90C | AWG | AWG | 60C | 75C | 90C | 60C | 75C | 90C | AWG
14 | 1.8 | 2.4 | 3 | -- | -- | -- | 14 | 14 | 3.6 | 4.8 | 6 | -- | -- | -- | 14 | 14 | 7.2 | 9.6 | 12 | -- | -- | -- | 14
12 | 2.4 | 3 | 3.6 | 1.8 | 2.4 | 3 | 12 | 12 | 4.8 | 6 | 7.2 | 3.6 | 4.8 | 6 | 12 | 12 | 9.6 | 12 | 14.4 | 7.2 | 9.6 | 12 | 12
10 | 3.6 | 4.2 | 4.8 | 3 | 3.6 | 4.2 | 10 | 10 | 7.2 | 8.4 | 9.6 | 6 | 7.2 | 8.4 | 10 | 10 | 14.4 | 16.8 | 19.2 | 12 | 14.4 | 16.8 | 10
8 | 4.8 | 6 | 6.6 | 4.2 | 4.8 | 5.4 | 8 | 8 | 9.6 | 12 | 13.2 | 8.4 | 9.6 | 10.8 | 8 | 8 | 19.2 | 24 | 26.4 | 16.8 | 19.2 | 21.6 | 8
6 | 6.6 | 7.8 | 9 | 4.8 | 6 | 6.6 | 6 | 6 | 13.2 | 15.6 | 18 | 9.6 | 12 | 13.2 | 6 | 6 | 26.4 | 31.2 | 36 | 19.2 | 24 | 26.4 | 6
4 | 8.4 | 10.2 | 11.4 | 6.6 | 7.8 | 9 | 4 | 4 | 16.8 | 20.4 | 22.8 | 13.2 | 15.6 | 18 | 4 | 4 | 33.6 | 40.8 | 45.6 | 26.4 | 31.2 | 36 | 4
3 | 10.2 | 12 | 13.8 | 7.8 | 9 | 10.2 | 3 | 3 | 20.4 | 24 | 27.6 | 15.6 | 18 | 20.4 | 3 | 3 | 40.8 | 48 | 55.2 | 31.2 | 36 | 40.8 | 3
2 | 11.4 | 13.8 | 15.6 | 9 | 10.8 | 12 | 2 | 2 | 22.8 | 27.6 | 31.2 | 18 | 21.6 | 24 | 2 | 2 | 45.6 | 55.2 | 62.4 | 36 | 43.2 | 48 | 2
1 | 13.2 | 15.6 | 17.4 | 10.2 | 12 | 13.8 | 1 | 1 | 26.4 | 31.2 | 34.8 | 20.4 | 24 | 27.6 | 1 | 1 | 52.8 | 62.4 | 69.6 | 40.8 | 48 | 55.2 | 1
1/O | 15 | 18 | 20.4 | 12 | 14.4 | 16.2 | 1/O | 1/O | 30 | 36 | 40.8 | 24 | 28.8 | 32.4 | 1/O | 1/O | 60 | 72 | 81.6 | 48 | 57.6 | 64.8 | 1/O
2/O | 17.4 | 21 | 23.4 | 13.8 | 16.2 | 18 | 2/O | 2/O | 34.8 | 42 | 46.8 | 27.6 | 32.4 | 36 | 2/O | 2/O | 69.6 | 84 | 93.6 | 55.2 | 64.8 | 72 | 2/O
3/O | 19.8 | 24 | 27 | 15.6 | 18.6 | 21 | 3/O | 3/O | 39.6 | 48 | 54 | 31.2 | 37.2 | 42 | 3/O | 3/O | 79.2 | 96 | 108 | 62.4 | 74.4 | 84 | 3/O
4/O | 23.4 | 27.6 | 31.2 | 18 | 21.6 | 24.6 | 4/O | 4/O | 46.8 | 55.2 | 62.4 | 36 | 43.2 | 49.2 | 4/O | 4/O | 93.6 | 110.4 | 124.8 | 72 | 86.4 | 98.4 | 4/O
250 | 25.8 | 30.6 | 34.8 | 20.4 | 24.6 | 27.6 | 250 | 250 | 51.6 | 61.2 | 69.6 | 40.8 | 49.2 | 55.2 | 250 | 250 | 103.2 | 122.4 | 139.2 | 81.6 | 98.4 | 110.4 | 250
300 | 28.8 | 34.2 | 38.4 | 23.4 | 27.6 | 31.2 | 300 | 300 | 57.6 | 68.4 | 76.8 | 46.8 | 55.2 | 62.4 | 300 | 300 | 115.2 | 136.8 | 153.6 | 93.6 | 110.4 | 124.8 | 300
350 | 31.2 | 37.2 | 42 | 25.2 | 30 | 33.6 | 350 | 350 | 62.4 | 74.4 | 84 | 50.4 | 60 | 67.2 | 350 | 350 | 124.8 | 148.8 | 168 | 100.8 | 120 | 134.4 | 350
400 | 33.6 | 40.2 | 45.6 | 27 | 32.4 | 36.6 | 400 | 400 | 67.2 | 80.4 | 91.2 | 54 | 64.8 | 73.2 | 400 | 400 | 134.4 | 160.8 | 182.4 | 108 | 129.6 | 146.4 | 400
500 | 38.4 | 45.6 | 51.6 | 31.2 | 37.2 | 42 | 500 | 500 | 76.8 | 91.2 | 103.2 | 62.4 | 74.4 | 84 | 500 | 500 | 153.6 | 182.4 | 206.4 | 124.8 | 148.8 | 168 | 500
600 | 42 | 50.4 | 57 | 34.2 | 40.8 | 46.2 | 600 | 600 | 84 | 100.8 | 114 | 68.4 | 81.6 | 92.4 | 600 | 600 | 168 | 201.6 | 228 | 136.8 | 163.2 | 184.8 | 600
700 | 46.2 | 55.2 | 62.4 | 37.8 | 45 | 51 | 700 | 700 | 92.4 | 110.4 | 124.8 | 75.6 | 90 | 102 | 700 | 700 | 184.8 | 220.8 | 249.6 | 151.2 | 180 | 204 | 700
750 | 48 | 57 | 64.2 | 38.4 | 46.2 | 52.2 | 750 | 750 | 96 | 114 | 128.4 | 76.8 | 92.4 | 104.4 | 750 | 750 | 192 | 228 | 256.8 | 153.6 | 184.8 | 208.8 | 750
800 | 49.2 | 58.8 | 66.6 | 39.6 | 47.4 | 53.4 | 800 | 800 | 98.4 | 117.6 | 133.2 | 79.2 | 94.8 | 106.8 | 800 | 800 | 196.8 | 235.2 | 266.4 | 158.4 | 189.6 | 213.6 | 800
900 | 52.2 | 62.4 | 70.2 | 42.6 | 51 | 57.6 | 900 | 900 | 104.4 | 124.8 | 140.4 | 85.2 | 102 | 115.2 | 900 | 900 | 208.8 | 249.6 | 280.8 | 170.4 | 204 | 230.4 | 900
1000 | 54.6 | 65.4 | 73.8 | 45 | 53.4 | 60 | 1000 | 1000 | 109.2 | 130.8 | 147.6 | 90 | 106.8 | 120 | 1000 | 1000 | 218.4 | 261.6 | 295.2 | 180 | 213.6 | 240 | 1000
1250 | 59.4 | 70.8 | 79.8 | 48.6 | 58.2 | 65.4 | 1250 | 1250 | 118.8 | 141.6 | 159.6 | 97.2 | 116.4 | 130.8 | 1250 | 1250 | 237.6 | 283.2 | 319.2 | 194.4 | 232.8 | 261.6 | 1250
1500 | 63 | 75 | 84.6 | 52.2 | 62.4 | 70.2 | 1500 | 1500 | 126 | 150 | 169.2 | 104.4 | 124.8 | 140.4 | 1500 | 1500 | 252 | 300 | 338.4 | 208.8 | 249.6 | 280.8 | 1500
1750 | 65.4 | 78 | 88.2 | 54.6 | 65.4 | 73.8 | 1750 | 1750 | 130.8 | 156 | 176.4 | 109.2 | 130.8 | 147.6 | 1750 | 1750 | 261.6 | 312 | 352.8 | 218.4 | 261.6 | 295.2 | 1750
2000 | 66.6 | 79.8 | 90 | 56.4 | 67.2 | 75.6 | 2000 | 2000 | 133.2 | 159.6 | 180 | 112.8 | 134.4 | 151.2 | 2000 | 2000 | 266.4 | 319.2 | 360 | 225.6 | 268.8 | 302.4 | 2000
MAX KVA AT 208 VAC, Three Phase, From Table 310.15 (B)(16) | [7 empty] | MAX KVA AT 480 VAC, Three Phase, From Table 310.15 (B)(16) | [7 empty] | Just Amperes, Table 310.15 (B)(16)
| CU |  |  | AL |  |  |  |  | CU |  |  | AL |  |  |  |  | CU |  |  | AL
AWG | 60C | 75C | 90C | 60C | 75C | 90C | AWG | AWG | 60C | 75C | 90C | 60C | 75C | 90C | AWG | AWG | 60C | 75C | 90C | 60C | 75C | 90C | AWG
14 | 5.404 | 7.2053 | 9.0067 | -- | -- | -- | 14 | 14 | 12.4708 | 16.6277 | 20.7846 | -- | -- | -- | 14 | 14 | 15 | 20 | 25 | -- | -- | -- | 14
12 | 7.2053 | 9.0067 | 10.808 | 5.404 | 7.2053 | 9.0067 | 12 | 12 | 16.6277 | 20.7846 | 24.9415 | 12.4708 | 16.6277 | 20.7846 | 12 | 12 | 20 | 25 | 30 | 15 | 20 | 25 | 12
10 | 10.808 | 12.6093 | 14.4107 | 9.0067 | 10.808 | 12.6093 | 10 | 10 | 24.9415 | 29.0985 | 33.2554 | 20.7846 | 24.9415 | 29.0985 | 10 | 10 | 30 | 35 | 40 | 25 | 30 | 35 | 10
8 | 14.4107 | 18.0133 | 19.8147 | 12.6093 | 14.4107 | 16.212 | 8 | 8 | 33.2554 | 41.5692 | 45.7261 | 29.0985 | 33.2554 | 37.4123 | 8 | 8 | 40 | 50 | 55 | 35 | 40 | 45 | 8
6 | 19.8147 | 23.4173 | 27.02 | 14.4107 | 18.0133 | 19.8147 | 6 | 6 | 45.7261 | 54.04 | 62.3538 | 33.2554 | 41.5692 | 45.7261 | 6 | 6 | 55 | 65 | 75 | 40 | 50 | 55 | 6
4 | 25.2187 | 30.6227 | 34.2253 | 19.8147 | 23.4173 | 27.02 | 4 | 4 | 58.1969 | 70.6677 | 78.9815 | 45.7261 | 54.04 | 62.3538 | 4 | 4 | 70 | 85 | 95 | 55 | 65 | 75 | 4
3 | 30.6227 | 36.0267 | 41.4307 | 23.4173 | 27.02 | 30.6227 | 3 | 3 | 70.6677 | 83.1384 | 95.6092 | 54.04 | 62.3538 | 70.6677 | 3 | 3 | 85 | 100 | 115 | 65 | 75 | 85 | 3
2 | 34.2253 | 41.4307 | 46.8347 | 27.02 | 32.424 | 36.0267 | 2 | 2 | 78.9815 | 95.6092 | 108.08 | 62.3538 | 74.8246 | 83.1384 | 2 | 2 | 95 | 115 | 130 | 75 | 90 | 100 | 2
1 | 39.6293 | 46.8347 | 52.2387 | 30.6227 | 36.0267 | 41.4307 | 1 | 1 | 91.4523 | 108.08 | 120.5507 | 70.6677 | 83.1384 | 95.6092 | 1 | 1 | 110 | 130 | 145 | 85 | 100 | 115 | 1
1/O | 45.0333 | 54.04 | 61.2453 | 36.0267 | 43.232 | 48.636 | 1/O | 1/O | 103.923 | 124.7077 | 141.3353 | 83.1384 | 99.7661 | 112.2369 | 1/O | 1/O | 125 | 150 | 170 | 100 | 120 | 135 | 1/O
2/O | 52.2387 | 63.0466 | 70.252 | 41.4307 | 48.636 | 54.04 | 2/O | 2/O | 120.5507 | 145.4923 | 162.12 | 95.6092 | 112.2369 | 124.7077 | 2/O | 2/O | 145 | 175 | 195 | 115 | 135 | 150 | 2/O
3/O | 59.444 | 72.0533 | 81.06 | 46.8347 | 55.8413 | 63.0466 | 3/O | 3/O | 137.1784 | 166.2769 | 187.0615 | 108.08 | 128.8646 | 145.4923 | 3/O | 3/O | 165 | 200 | 225 | 130 | 155 | 175 | 3/O
4/O | 70.252 | 82.8613 | 93.6693 | 54.04 | 64.848 | 73.8546 | 4/O | 4/O | 162.12 | 191.2184 | 216.1599 | 124.7077 | 149.6492 | 170.4338 | 4/O | 4/O | 195 | 230 | 260 | 150 | 180 | 205 | 4/O
250 | 77.4573 | 91.868 | 104.4773 | 61.2453 | 73.8546 | 82.8613 | 250 | 250 | 178.7476 | 212.003 | 241.1015 | 141.3353 | 170.4338 | 191.2184 | 250 | 250 | 215 | 255 | 290 | 170 | 205 | 230 | 250
300 | 86.464 | 102.676 | 115.2853 | 70.252 | 82.8613 | 93.6693 | 300 | 300 | 199.5323 | 236.9446 | 266.043 | 162.12 | 191.2184 | 216.1599 | 300 | 300 | 240 | 285 | 320 | 195 | 230 | 260 | 300
350 | 93.6693 | 111.6826 | 126.0933 | 75.656 | 90.0666 | 100.8746 | 350 | 350 | 216.1599 | 257.7292 | 290.9845 | 174.5907 | 207.8461 | 232.7876 | 350 | 350 | 260 | 310 | 350 | 210 | 250 | 280 | 350
400 | 100.8746 | 120.6893 | 136.9013 | 81.06 | 97.272 | 109.8813 | 400 | 400 | 232.7876 | 278.5138 | 315.9261 | 187.0615 | 224.4738 | 253.5722 | 400 | 400 | 280 | 335 | 380 | 225 | 270 | 305 | 400
500 | 115.2853 | 136.9013 | 154.9146 | 93.6693 | 111.6826 | 126.0933 | 500 | 500 | 266.043 | 315.9261 | 357.4953 | 216.1599 | 257.7292 | 290.9845 | 500 | 500 | 320 | 380 | 430 | 260 | 310 | 350 | 500
600 | 126.0933 | 151.312 | 171.1266 | 102.676 | 122.4906 | 138.7026 | 600 | 600 | 290.9845 | 349.1814 | 394.9076 | 236.9446 | 282.6707 | 320.083 | 600 | 600 | 350 | 420 | 475 | 285 | 340 | 385 | 600
700 | 138.7026 | 165.7226 | 187.3386 | 113.484 | 135.1 | 153.1133 | 700 | 700 | 320.083 | 382.4368 | 432.3199 | 261.8861 | 311.7691 | 353.3384 | 700 | 700 | 385 | 460 | 520 | 315 | 375 | 425 | 700
750 | 144.1066 | 171.1266 | 192.7426 | 115.2853 | 138.7026 | 156.716 | 750 | 750 | 332.5538 | 394.9076 | 444.7906 | 266.043 | 320.083 | 361.6522 | 750 | 750 | 400 | 475 | 535 | 320 | 385 | 435 | 750
800 | 147.7093 | 176.5306 | 199.9479 | 118.888 | 142.3053 | 160.3186 | 800 | 800 | 340.8676 | 407.3783 | 461.4183 | 274.3568 | 328.3968 | 369.9661 | 800 | 800 | 410 | 490 | 555 | 330 | 395 | 445 | 800
900 | 156.716 | 187.3386 | 210.7559 | 127.8946 | 153.1133 | 172.928 | 900 | 900 | 361.6522 | 432.3199 | 486.3599 | 295.1415 | 353.3384 | 399.0645 | 900 | 900 | 435 | 520 | 585 | 355 | 425 | 480 | 900
1000 | 163.9213 | 196.3453 | 221.5639 | 135.1 | 160.3186 | 180.1333 | 1000 | 1000 | 378.2799 | 453.1045 | 511.3014 | 311.7691 | 369.9661 | 415.6922 | 1000 | 1000 | 455 | 545 | 615 | 375 | 445 | 500 | 1000
1250 | 178.332 | 212.5573 | 239.5773 | 145.908 | 174.7293 | 196.3453 | 1250 | 1250 | 411.5353 | 490.5168 | 552.8706 | 336.7107 | 403.2214 | 453.1045 | 1250 | 1250 | 495 | 590 | 665 | 405 | 485 | 545 | 1250
1500 | 189.1399 | 225.1666 | 253.9879 | 156.716 | 187.3386 | 210.7559 | 1500 | 1500 | 436.4768 | 519.6152 | 586.126 | 361.6522 | 432.3199 | 486.3599 | 1500 | 1500 | 525 | 625 | 705 | 435 | 520 | 585 | 1500
1750 | 196.3453 | 234.1733 | 264.7959 | 163.9213 | 196.3453 | 221.5639 | 1750 | 1750 | 453.1045 | 540.3999 | 611.0675 | 378.2799 | 453.1045 | 511.3014 | 1750 | 1750 | 545 | 650 | 735 | 455 | 545 | 615 | 1750
2000 | 199.9479 | 239.5773 | 270.1999 | 169.3253 | 201.7493 | 226.9679 | 2000 | 2000 | 461.4183 | 552.8706 | 623.5383 | 390.7507 | 465.5753 | 523.7722 | 2000 | 2000 | 555 | 665 | 750 | 470 | 560 | 630 | 2000